## Overview
Title: | Fluoride Implementation Estimate - Preliminary Estimate Update
Project Name: | Concept Plan to implement Fluoridation of the Christchurch Drinking Water Supplies
Project Number: | IA273800
Document Number: | IA273800-0001-BW-EST-0001
Date: | 2022-Mar-10
Prepared by: | Silvia Vlad, Jack Deely
Reviewed by: | Becky MacDonald, Richard Greenwood

## Comment Tracking
| Project Name: | Concept Plan to Implement Fluoridation of the Christchurch Drinking Water Supplies
| Deliverable: | Implementation Estimate - Preliminary Update
| Commenters: | Laco Yan (LY), Gijs Hovens (GH)
| Responders: | Silvia Vlad (SV), Becky MacDonald (BM), Richard Greenwood (RG)
| Date: | 2022-03-09
Comment Number | Reference Page, Section No. | City's Comment | Commenter | Consultant's Response
1 | P6 of the power point file | The Estimation of Process Cost is the basis of the entire estimation. It is recommended to check into details and cover all elements, not only pumps and equipment, but also pipes, valves, fittings, and associate material. | Laco Yan | Noted. The process cost includes a $7,800 allowance for pipes and fittings, at a reference cost of approximately $300/m for pipe-in-pipe configuration.
2 | P6 of the power point file | The allowance of Installation cost (15% to equipment cost) is low. Based on the previous experience, the budget of mechanical installation cost in PS is around 25-30%. | Laco Yan | The estimate has been updated accordingly
3 | P7 of the power point file | Building expansion (if Required). This is a high risk scope due to the expensive cost. It is recommended to have more specified information, for example the area requirement of each unit. Allowance to be made based on the “new area”. | Laco Yan | The building area estimate is based on a 4x4m space for the small and medium sized facilities, and a 4x5m space for the large facilities, with a reference cost of $2000/m2, including reinforced concrete foundations, walls, roofing and doors.
4 | P15 of the power point file | Mechanical installation cost is missing from the tab. Is it covered in the process equipment? | Laco Yan | The estimate has been updated to include additional budget for the installation of building mechanical equipment. Installation of process and instrumentation equipment is included in the process subtotal, at a rate of 30%.
5 | P15 of the power point file | Commissioning is missing | Laco Yan | Commissioning has been broken out separately from the other costs to clarify. Estimated based on reference projects to be approximately 100 hours per site
6 | P16 of the power point file | The allowance of P&G is high. From HDM and previous project, the overhead is approx 15-18% | Laco Yan | The recommendation is noted. However, a 30% allowance is recommended given the complexity and number of contractors who will be engaged to complete the work
7 | P17 of the power point file | The % to Engineering shall includes the investigation. | Laco Yan | The estimate has been updated to include additional budget for the investigation stage.
8 | P17 of the power point file | given that this is permanent what is the estimated depreciation rate? Where is this reflected via an annual estimated renewals budget? | Laco Yan | The estimate has been updated accordingly
9 | P17 of the power point file | CCC Internal Staff PM 2% is low, recommend 4%. | Laco Yan | The estimate has been updated accordingly
10 | P18 of the power point file | Contingency 30% is reasonable for estimation at this stage. | Laco Yan | Noted.
11 | P18 of the power point file | Escalation 1 year. Is there any basis for this figure 5%? It is recommended to apply the figure from Stat NZ Heavy and civil engineering construction %. | Laco Yan | We are currently seeing significant escalation in equipment and materials costs both globally and regionally. Average increase in the NZ Heavy and civil engineering construction index has been >4%/year since 2019, and the most recent quarterly increase is indicative of 9% inflation from December 2020 to December 2021. A minimum rate of 5% (or greater) is recommended
12 | P18 of the power point file | Escalation. Why it is only for one year. In the Schedule, it shows a 3 year construction period. | Laco Yan | The schedule was updated based on equipment lead times which we were still awaiting. The estimate has been updated to include 28 month’s escalation based on a midpoint of construction in July 2024
13 | Process/ Instrumentation - Capital Direct | Confirm that this includes allowance for suitable security/bunding at dosing points to prevent spill and vandalism. Confirm this includes suitable allowance for fittings (dosing systems can use a LOT of fittings) | Gijs Hovens | The estimate includes $8,000-10,000 for bunding (Depending on system size) and a $15k security allowance (captured under the miscellaneous subtotal) The estimate also includes a $7,800 allowance for piping and fittings
14 | Building/Civil - Capital Direct | Suggest base estimate is explicit that it excludes cost escalations for any accidental asbestos or contaminated materials discovery (we got badly burnt for this at places like Avonhead, Trafalgar, etc.. when wellhead raising). | Gijs Hovens | Noted. The estimate does not include designated substance/asbestos abatement, and this is noted in the revised line item title.
15 | Misc - Capital Direct | Is there an allowance for SCADA critical spares? | Gijs Hovens | The estimate includes an allowance for critical spares including instrumentation, and has been updated to include a $5k allowance/site for SCADA critical spares
16 | Capital non-xn | $40k comm’s protocol says “by site” – which seems to indicate it is more as a direct cost (software/hardware?) under IEC (and therefore subject to the markups)? | Gijs Hovens | This is a question to flag for Karn. When he provided the initial estimate he noted it was for time on site, but there may be hardware/software components of the cost.
17 | Capital non-xn | Documentation updates (1 week per facility) might work if just taking the Asset Management view; for the Operations/Maintenance documentation I would suggest you’ll need an additional 2 weeks per facility if you want P&ID’s, O&M manuals, field labelling, GIS updates, OEM manuals, SSRMP plans, SOP’s, contractor servicing plans, operational and compliance checklists all collated and verified. | Gijs Hovens | The estimate has been updated accordingly
18 | Capital non-xn | 10 days training at $10,000 feels light for training up staff in the hazards of chemical handling (Certified Handlers). Would suggest that this would be a week per person due to the level of chemical risk. At 5 people this is likely to be closer to $35,000. | Gijs Hovens | The update has been updated to include a $35,000 training budget, which breaks down to 5 days for 7 people based on the hourly rate assumed.
19 | Capital non-xn | Include $5,000 for chemical/safety labelling. | Gijs Hovens | Supplier labelling is included in the process equipment cost. The estimate has been updated to include a further $5,000 budget for CCC-specific labelling
20 | O&M - Chemical | • Be explicit that this is at current pricing, presume that pricing is subject to fluctuation on no less than quarterly basis? • Allow 16 hours FTE time per annum for contract management • Allow 16 hours FTE time for PO/invoice processing | Gijs Hovens | The estimate has been updated accordingly The estimate has been updated accordingly, with an additional 16 hours for managing a second contract for container disposal. The estimate has been updated accordingly with an additional 16 hours for PO/invoice processing for the disposal contract
21 | O&M - Slide 19 (page 22) Compliance | Weekly fluoride analysis: • 0.5FTE at $380k therefore 1 FTE is $600k/annum. Even at 50% loading this is $300k/annum. Where do I sign up? | Gijs Hovens | This was a transcription error from the calculations sheet to the power point slides, apologies for the confusion. At a standard rate of $125/hr, the 0.5 FTE line item should total $146,250.
22 | O&M - Slide 19 (page 23) Compliance | Weekly fluoride analysis: 0.5FTE at $380k therefore 1 FTE is $600k/annum. Even at 50% loading this is $300k/annum. Where do I sign up? | Gijs Hovens | This was a transcription error from the calculations sheet to the power point slides, apologies for the confusion. At a standard rate of $125/hr, the 0.5 FTE line item should total $146,250.
23 | O&M Other | Given that this is permanent what is the estimated depreciation rate? Where is this reflected via an annual estimated renewals budget? | Gijs Hovens | For depreciation, the assets would depriciate to zero over the course of their useful lives. For state-of-good-repair/renewals budgeting purposes, we would suggest the following mid-life intervention and end-of-life-replacement timelines: - Liquid chemical system: replace at 10 years (typically assumed at 20 years, but given our experience on similar projects, a 10 year life span is more appropriate for the corrosive nature of HFA) - Appurtenances of the system (e.g. piping, tanks): review and replace as required at 10 years - Scrubber media for a passive scrubber: replace at 5 years. - Air handling units and misc. building mechanical: mid-life intervention at 15 years, replace at 25 years - Miscellaneous electrical: replace at 30 years - Health and safety equipment: replace at 10 years - Analyzers, indicators, analytical instruments and misc. instrumentation: replace at 10-15 - years, assume 10 years - Misc. site works: intervention at 40 years - Signage: replace at 20 years - Security: replace 8 years based on obsolescence - Misc. light structural: mid-life intervention every 10 years, replace at 40 years Based on these assumptions, the estimate has been updated andan annualized sate-of-good-repair cost of $1,058,000 is anticipated, including the same project cost markups as included in capital estimate

## Estimate Summary
Estimate Summary
Item | Basis | Small | Medium | Large
Process |  | 196000 | 223000 | 282000
Building Mechanical |  | 15000 | 15000 | 15000
Structural |  | 32000 | 32000 | 40000
Civil |  | 60000 | to | 107000
Electrical |  | 30000 | 30000 | 43000
I&C |  | 60000 | 60000 | 60000
Miscellaneous |  | 33000 | 33000 | 33000
Direct Cost Subtotal |  | 443000 | 470000 | 550000
Preliminary & General Cost, Mobilization & Demobilization, Overhead and Profit | 30% | 133000 | 141000 | 165000
Contractor Overhead, Profit and Risk | 15% | 67000 | 71000 | 83000
Warranty (Defects Liability Period) | 2% | 9000 | 10000 | 11000
Construction Value Subtotal |  | 652000 | 692000 | 809000
Item | Basis | Total for All Facilities | Average Per facility
Construction Value Subtotal |  | 29563000 | 656955.5556
Permitting & Consents | 2% | 592000 | 13155.5556
Engineering | 13% | 3844000 | 85422.2222
Services During Construction – inspection, contract administration | 7% | 2070000 | 46000
CCC Internal Program Management | 4% | 1183000 | 26288.8889
Documentation Updates – reports, asset management systems, drawing repositories | 1 week per facility | 675000 | 15000
SCADA Template development | 12 weeks total | 60000 | 1333.3333
SCADA Upgrade – communications protocol | $40,000 per site | 1800000 | 40000
Training | 10 days | 35000 | 777.7778
Non-Construction Implementation Costs |  | 10304000 | 228977.7778
Capital Cost | Multiplier | Total for All Facilities | Average per Facility |  | Capital Cost | Akaroa | Brooklands / Kainga | Christchurch | Lyttelton | Total | Check
Direct Cost Subtotal |  | 20065000 | 445888.8889 |  | Direct Cost Subtotal | 395000 | 801000 | 18869000 | 0 | 20065000 | Pass
Markups | 47% | 9498000 | 211066.6667 |  | Markups | 187000 | 379000 | 8932000 | 0 | 9498000 | Pass
Construction Value Subtotal |  | 29563000 | 656955.5556 |  | Construction Value Subtotal | 582000 | 1180000 | 27801000 | 0 | 29563000 | Pass
Non-Construction Implementation Costs | 34.85% | 10304000 | 228977.7778 |  | Non-Construction Implementation Costs | 202852.4845 | 411281.6697 | 9689865.8458 | 0 | 10304000 | Pass
Base Estimate |  | 39867000 | 885933.3333 |  | Base Estimate | 784852.4845 | 1591281.6697 | 37490865.8458 | 0 | 39867000 | Pass
Contingency | 30% | 11961000 | 265800 |  | Contingency | 235500 | 477400 | 11247300 | 0 | 11961000 | Pass
Project Estimate |  | 51828000 | 1151733.3333 |  | Project Estimate | 1020352.4845 | 2068681.6697 | 48738165.8458 | 0 | 51828000 | Pass
Escalation | 5% | 6250000 | 138888.8889 |  | Escalation | 123045.5165 | 249464.7765 | 5877393.2341 | 0 | 6250000 | Pass
Total Outrun Cost Estimate |  | 58078000 | 1290622.2222 |  | Total Outrun Cost Estimate | 1143398.001 | 2318146.4461 | 54615559.0799 | 0 | 58078000 | Pass
Chemical Supply, Delivery and Waste Disposal | Annual Estimate
Total annual flow (m3/yr) | 58196000
Volume of chemical used per year (L/yr) | 239000
Chemical cost, delivered ($/yr) | 587000
Container disposal ($/yr) | 121600
Contract management | 4000
PO and invoice processing | 4000
Chemical Supply, Delivery & Waste Disposal Subtotal | 716600
O&M Cost | Annual Estimate
Chemical Supply, Delivery & Waste Disposal Subtotal | 716600
Compliance Management, Maintenance and Inspection Subtotal | 1135000
Total O&M Cost Estimate - All facilities | 1851600
State of Good Repair/Renewals | Annual Estimate
Annualized cost | 1062162.9167

## Estimate Breakdown
Cost Breakdown | [11 empty] | By Facility
updates per CCC comments
Estimate Basis |  |  | System Size | [10 empty] | Facility
| Parameter | Units | Small | Medium | Large |  |  | Notes |  |  |  |  | Potential Designations | Thompsons | Avonhead | Belfast | Burnside | Crosbie | Farrington | Grampian | Jeffreys | Redwood | Wrights | Gardiners | Aston | Effingham | Keyes | Lake Terrace | Carters | Estuary | Sockburn | Denton | Wilmers | Dunbars | Main Pumps WS | Addington | Aldwins | Blighs | Grassmere | Hillmorton | Hills | Mays | Montreal | Spreydon | Sydenham | Trafalgar | Worcester | Tanner | Picton | Tara | St Johns | Woolston | Marshlands | Parklands | Prestons | Brooklands | Kainga | Akaroa L’Aube Hill WTP
| Max Flow | m3/hr | 300.4 | 600 | 1320 | [6 empty] | Capacity Future (m3/hr) |  | 350 | 374 | 380 | 845 | 512 | 918.5568 | 450 | 500 | 424.8 | 356 | 350 | 285 | 321 | 580 | 485 | 551 | 277 | 1320 | 1100 | 470 | 1149.984 | 1000 | 252 | 280 | 280 | 528 | 300 | 580 | 550 | 449 | 450 | 450 | 450 | 511 | 137 | 557.6776 | 120 | 666.6667 | 545 | 440 | 500 | 768 | 180 | 108 | 87.5
| Avg. Flow | m3/hr | 100.1333 | 200 | 440 |  |  | per Michele, estimated at 1/3 of peak flow |  |  |  | Avg. flow (based on 30% of future capacity) (m3/hr) |  | 105 | 112.2 | 114 | 253.5 | 153.6 | 275.567 | 135 | 150 | 127.44 | 106.8 | 105 | 85.5 | 96.3 | 174 | 145.5 | 165.3 | 83.1 | 396 | 330 | 141 | 344.9952 | 300 | 75.6 | 84 | 84 | 158.4 | 90 | 174 | 165 | 134.7 | 135 | 135 | 135 | 153.3 | 41.1 | 167.3033 | 36 | 200 | 163.5 | 132 | 150 | 230.4 | 54 | 32.4 | 26.25
| minimum bulk storage tank volume | L | 137.5439 | 265.9183 | 605.1934 |  |  | based on 2 weeks' storage at average flow, average dose |  |  |  | Facility Size designation |  | Medium | Medium | Medium | Large | Medium | Large | Medium | Medium | Medium | Medium | Medium | Small | Medium | Medium | Medium | Medium | Small | Large | Large | Medium | Large | Large | Small | Small | Small | Medium | Small | Medium | Medium | Medium | Medium | Medium | Medium | Medium | Small | Medium | Small | Large | Medium | Medium | Medium | Large | Small | Small | Small
| Bulk tank capacity | L | 600 | 600 | 1500 |  |  | based on sizing available from Filtec |  |  |  | Mixer required | Yes/no | Yes | Yes | No | No | No | Yes | No | No | No | Yes | No | Yes | Yes | No | Yes | Yes | No | Yes | No | Yes | No | No | Yes | Yes | No | No | No | Yes | Yes | Yes | Yes | Yes | No | No | No | No | Yes | Yes | Yes | No | No | No | No | No | No
| minimum day tank volume | L | 32.7486 | 63.3139 | 144.0937 |  |  | based on 24 hours at max flow, max dose |  |  |  | Building expansion required | yes/no | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| day tank capacity | L | 50 | 100 | 200 |  |  | based on sizing available from Filtec |  |  |  | tree removal required | Yes/no | No | No | Yes | Yes | No | Yes | No | No | No | Yes | No | No | No | No | No | Yes | No | No | No | Yes | No | No | Yes | No | Yes | No | No | No | No | No | Yes | No | No | Yes | Yes | No | Yes | Yes | Yes | No | No | No | Yes | No | No
| no. metering pumps |  | 2 | 2 | 2 |  |  | duty/standby |  |  |  | overall site constraints | none/minor/medium/high | None | None | Medium | None | None | None | None | None | Medium | None | None | None | None | None | Medium | High | High | None | None | Minor | None | N/A | Medium | None | None | Medium | High | High | High | Minor | None | None | None | Medium | None | None | None | None | Medium | None | None | None | None | None | No
| no. transfer pumps |  | 2 | 2 | 2 |  |  | confirm if duty/standby is needed |  |  |  | markup - Delivery Constraint | none/minor/medium | None | None | Minor | None | Minor | None | None | Minor | None | None | None | None | Minor | None | None | Medium | Medium | None | Minor | None | Minor | None | Minor | None | None | Minor | Minor | None | Minor | None | None | None | Medium | Minor | None | Minor | None | None | Medium | Minor | Minor | None | None | None | None
| no. carrier water pumps |  | 2 | 2 | 2 |  |  | confirm if duty/standby is needed |  |  |  | markup - WW connection | on site, on road, far, none | None | At Road | At Road | Far | Far | At Road | At Road | Far | At Road | At Road | Far | On Site | At Road | At Road | At Road | At Road | At Road | Far | Far | None | At Road | At Road | At Road | At Road | At Road | At Road | At Road | At Road | On Site | At Road | At Road | Far | Far | At Road | At Road | Far | At Road | At Road | At Road | Far | Far | At Road | At Road | On Site | On Site
| footprint | m2 | 16 | 16 | 20 |  |  | larger footprint required for large system as bulk tank footprint will be larger |  |  |  | Water Supply Area | Christchurch, Brooklands Kainga, Akaroa | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Christchurch | Brooklands / Kainga | Brooklands / Kainga | Akaroa
| Carrier water flow | L/s | 0.04 | 0.08 | 0.17 |  |  | based on 1:100 dilution
|  | L/hr | 144 | 288 | 612
| no. PS of this size |  | 11 | 26 | 8
| Constants | Value | Units |  |  |  |  | Notes
| Labour | 125 | $/hr
| Target fluoride dose | 0.9 | mg/L
| HFA, delivered | 2.46 | $/L |  |  |  |  | Ixom quote. Redox was not able to provide an estimate
|  | 11.1891 | $/kg
| HFA delivery container disposal cost | 100 | $/container |  |  |  |  | placeholder value, approximately 20% of the delivery cost. Typically on a $/kg basis. Awaiting quote from Envirowaste
| HFA active chemical concentration | 0.21986 | kg/L
*** note that cost estimate does not account for potential bulk/program discounts
Capital Cost Estimate
| Item | % markups | Small System Cost | Medium System Cost | Large System Cost | All Facilities | Source | Notes | % of Capital Subtotal | Renewal Category |  | Item | [46 empty] | TOTAL - all facilities
Process Equipment
| Bulk Tank |  | 7500 | 7500 | 10000 |  | Filtec | not including bunding |  | Appurtenances of the system (e.g. piping, tanks) |  | Bulk Tank |  | 7500 | 7500 | 7500 | 10000 | 7500 | 10000 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 10000 | 10000 | 7500 | 10000 | 10000 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 10000 | 7500 | 7500 | 7500 | 10000 | 7500 | 7500 | 7500 | 357500
| Day Tank |  | 3000 | 5000 | 8000 |  | Filtec | not including bunding |  | Appurtenances of the system (e.g. piping, tanks) |  | Day Tank |  | 5000 | 5000 | 5000 | 8000 | 5000 | 8000 | 5000 | 5000 | 5000 | 5000 | 5000 | 3000 | 5000 | 5000 | 5000 | 5000 | 3000 | 8000 | 8000 | 5000 | 8000 | 8000 | 3000 | 3000 | 3000 | 5000 | 3000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 3000 | 5000 | 3000 | 8000 | 5000 | 5000 | 5000 | 8000 | 3000 | 3000 | 3000 | 227000
| Dosing skid including pumps |  | 26000 | 43000 | 68000 |  | Scaled from vendor quotes |  |  | Liquid chemical system |  | Dosing skid including pumps |  | 43000 | 43000 | 43000 | 68000 | 43000 | 68000 | 43000 | 43000 | 43000 | 43000 | 43000 | 26000 | 43000 | 43000 | 43000 | 43000 | 26000 | 68000 | 68000 | 43000 | 68000 | 68000 | 26000 | 26000 | 26000 | 43000 | 26000 | 43000 | 43000 | 43000 | 43000 | 43000 | 43000 | 43000 | 26000 | 43000 | 26000 | 68000 | 43000 | 43000 | 43000 | 68000 | 26000 | 26000 | 26000 | 1948000
| Transfer pump |  | 7500 | 7500 | 12500 |  | Filtec |  |  | Appurtenances of the system (e.g. piping, tanks) |  | Transfer pump |  | 7500 | 7500 | 7500 | 12500 | 7500 | 12500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 12500 | 12500 | 7500 | 12500 | 12500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 7500 | 12500 | 7500 | 7500 | 7500 | 12500 | 7500 | 7500 | 7500 | 377500
| Analyser |  | 17500 | 17500 | 17500 |  | Filtec |  |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Analyser |  | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 787500
| Ultrasonic level indicator |  | 2000 | 2000 | 2000 |  | ChemFeed | one for each day tank and bulk tank |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Ultrasonic level indicator |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 90000
| Ultrasonic level switch |  | 2000 | 2000 | 2000 |  | ChemFeed | two for each day tank and bulk tank (H and L) |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Ultrasonic level switch |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 90000
| Tanker loading station for engineered tanks |  | 3000 | 3000 | 3000 |  | ChemFeed |  |  | Appurtenances of the system (e.g. piping, tanks) |  | Tanker loading station for engineered tanks |  | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 135000
| Leak detection switch x2 |  | 600 | 600 | 600 |  | ChemFeed | for the bunded area and the containment pipe |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Leak detection switch x2 |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 27000
| Carrier water pumps |  | 10000 | 10000 | 10000 |  |  |  |  | Appurtenances of the system (e.g. piping, tanks) |  | Carrier water pumps |  | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 450000
| Bunding |  | 8000 | 8000 | 10000 |  | Scaled from vendor quotes | Prefabricated bunds purchasing and delivery to site. Allowance for concrete coating for spills, etc. |  | Appurtenances of the system (e.g. piping, tanks) |  | Bunding |  | 8000 | 8000 | 8000 | 10000 | 8000 | 10000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 10000 | 10000 | 8000 | 10000 | 10000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 8000 | 10000 | 8000 | 8000 | 8000 | 10000 | 8000 | 8000 | 8000 | 376000
| waste tank |  | 2000 | 2000 | 2000 |  |  |  |  | Appurtenances of the system (e.g. piping, tanks) |  | waste tank |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 90000
| Injection quill |  | 1000 | 1000 | 1000 |  |  | Corporation style lance |  | Appurtenances of the system (e.g. piping, tanks) |  | Injection quill |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 45000
| Piping, Fittings and Pipe Tap |  | 7800 | 7800 | 7800 |  | reference projects | sampling pipework and additional 6 K for pipng and fittings (approx 20 m of pipe at $300/m). |  | Appurtenances of the system (e.g. piping, tanks) |  | Piping, Fittings and Pipe Tap |  | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 7800 | 351000
| Safety shower |  | 7000 | 7000 | 7000 |  | Filtec |  |  | Appurtenances of the system (e.g. piping, tanks) | Health and safety equipment | Safety shower |  | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 7000 | 315000
| Scrubber |  | 1000 | 1000 | 1000 |  | ChemFeed |  |  | Scrubber media for a passive scrubber |  | Scrubber |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 45000
| Vapour detection |  | 5000 | 5000 | 5000 |  | ChemFeed |  |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Vapour detection |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 225000
| Chemical Delivery Panel |  | 5000 | 5000 | 5000 |  | reference project |  |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Chemical Delivery Panel |  | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 225000
| Flow Meter |  | 17500 | 17500 | 22500 |  | Filtec |  |  | Analyzers, indicators, analytical instruments and misc. instrumentation |  | Flow Meter |  | 17500 | 17500 | 17500 | 22500 | 17500 | 22500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 22500 | 22500 | 17500 | 22500 | 22500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 17500 | 22500 | 17500 | 17500 | 17500 | 22500 | 17500 | 17500 | 17500 | 827500
| Mixer | include if required | 3300 | 3300 | 3300 |  | reference project |  |  | Appurtenances of the system (e.g. piping, tanks) |  | Mixer | include if required | 3300 | 3300 | 0 | 0 | 0 | 3300 | 0 | 3300 | 0 | 3300 | 0 | 3300 | 3300 | 0 | 3300 | 3300 | 0 | 3300 | 0 | 3300 | 0 | 0 | 3300 | 3300 | 0 | 0 | 0 | 3300 | 3300 | 3300 | 3300 | 3300 | 0 | 0 | 0 | 0 | 3300 | 3300 | 3300 | 0 | 0 | 0 | 0 | 0 | 0 | 69300
| Personal Protective Equipment |  | 4000 | 4000 | 4000 |  |  |  |  | Health and safety equipment |  | Personal Protective Equipment |  | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 180000
| Critical Spares | 10% | 14100 | 16000 | 20300 |  | reference project | 10% of process equipment cost |  | N/A |  | Critical Spares |  | 16000 | 16000 | 16000 | 20300 | 16000 | 20300 | 16000 | 16000 | 16000 | 16000 | 16000 | 14100 | 16000 | 16000 | 16000 | 16000 | 14100 | 20300 | 20300 | 16000 | 20300 | 20300 | 14100 | 14100 | 14100 | 16000 | 14100 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 16000 | 14100 | 16000 | 14100 | 20300 | 16000 | 16000 | 16000 | 20300 | 14100 | 14100 | 14100 | 733500
| Installation | 30% | 41100 | 46800 | 59500 |  | reference project | updated to 30% per CCC estimating engineer |  | N/A |  | Installation |  | 46800 | 46800 | 46800 | 59500 | 46800 | 59500 | 46800 | 46800 | 46800 | 46800 | 46800 | 41100 | 46800 | 46800 | 46800 | 46800 | 41100 | 59500 | 59500 | 46800 | 59500 | 59500 | 41100 | 41100 | 41100 | 46800 | 41100 | 46800 | 46800 | 46800 | 46800 | 46800 | 46800 | 46800 | 41100 | 46800 | 41100 | 59500 | 46800 | 46800 | 46800 | 59500 | 41100 | 41100 | 41100 | 2144900
| Process Subtotal |  | 196000 | 223000 | 282000 |  |  |  | 51.27% |  |  | Process Subtotal |  | 223000 | 223000 | 220000 | 279000 | 220000 | 282000 | 220000 | 223000 | 220000 | 223000 | 220000 | 196000 | 223000 | 220000 | 223000 | 223000 | 193000 | 282000 | 279000 | 223000 | 279000 | 279000 | 196000 | 196000 | 193000 | 220000 | 193000 | 223000 | 223000 | 223000 | 223000 | 223000 | 220000 | 220000 | 193000 | 220000 | 196000 | 282000 | 223000 | 220000 | 220000 | 279000 | 193000 | 193000 | 193000 | 10138000
| Mechanical | [10 empty] | Mechanical
| Mechanical Allowance (ventillation, heating, including installation) |  | 15000 | 15000 | 15000 |  | reference project | Allowance. Including ventilation (extractor fan. Separate scrubber system allowance in process equipment), heating to prevent freezing, allowance for installation added per CCC comment |  | Air handling units and misc. building mechanical |  | Mechanical Allowance (ventillation, heating, including installation) |  | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 675000
| Mechanical Subtotal |  | 15000 | 15000 | 15000 |  |  |  | 0% |  |  | Mechanical Subtotal |  | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 675000
| Structural | [10 empty] | Structural
| Building expansion. Excludes designated substance/asbestos abatement | include if required | 32000 | 32000 | 40000 |  | reference project | Based on Kingston unit rate, with markup for smaller facilities ($2k/m2). Includes RC foundations, walls, roof, doors. Include if required | 7.273% | Misc. light structural |  | Building expansion. Excludes designated substance/asbestos abatement | include if required | 32000 | 32000 | 32000 | 40000 | 32000 | 40000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 40000 | 40000 | 0 | 40000 | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 40000 | 32000 | 32000 | 32000 | 40000 | 32000 | 32000 | 32000 | 1432000
| Structural Subtotal |  | 32000 | 32000 | 40000 | [6 empty] | Structural Subtotal |  | 32000 | 32000 | 32000 | 40000 | 32000 | 40000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 40000 | 40000 | 0 | 40000 | 0 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 32000 | 40000 | 32000 | 32000 | 32000 | 40000 | 32000 | 32000 | 32000 | 1432000
| Civil | [10 empty] | Civil
| Civil Allowance (trenching, identification of buried services, site reinstatement) |  | 60000 | 60000 | 60000 |  | reference projects | Allowance. Includes trenching for dosing and analyzer lines, delivery pad, identification of buried services, site reinstatement. |  | Misc. site works |  | Civil Allowance (trenching, identification of buried services, site reinstatement) |  | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 60000 | 2700000
| tree removal | include if required | 5000 | 5000 | 5000 |  |  | allowance, include if needed |  | Misc. site works |  | tree removal | include if required |  |  | 5000 | 5000 |  | 5000 |  |  |  | 5000 | [5 empty] | 5000 |  |  |  | 5000 |  |  | 5000 |  | 5000 | [5 empty] | 5000 |  |  | 5000 | 5000 |  | 5000 | 5000 | 5000 |  |  |  | 5000 |  |  | 75000
| overall site constraints | include if required | [7 empty] | Misc. site works |  | overall site constraints | include if required | [45 empty] | 0
| minor | 10% | 6000 | 6000 | 6000 |  |  |  |  | Misc. site works |  | minor | 10% | [19 empty] | 6000 | [9 empty] | 6000 | [15 empty] | 12000
| medium | 25% | 15000 | 15000 | 15000 |  |  |  |  | Misc. site works |  | medium | 25% |  |  | 15000 | [5 empty] | 15000 | [5 empty] | 15000 | [7 empty] | 15000 |  |  | 15000 | [7 empty] | 15000 |  |  |  |  | 15000 | [6 empty] | 105000
| high | 40% | 24000 | 24000 | 24000 |  |  |  |  | Misc. site works |  | high | 40% | [15 empty] | 24000 | 24000 | [9 empty] | 24000 | 24000 | 24000 | [16 empty] | 120000
| markup - Delivery Constraint | include if required | [7 empty] | Misc. site works |  | markup - Delivery Constraint | include if required | [45 empty] | 0
| minor | 10% | 6000 | 6000 | 6000 |  |  |  |  | Misc. site works |  | minor | 10% |  |  | 6000 |  | 6000 |  |  | 6000 |  |  |  |  | 6000 | [5 empty] | 6000 |  | 6000 |  | 6000 |  |  | 6000 | 6000 |  | 6000 |  |  |  |  | 6000 |  | 6000 |  |  |  | 6000 | 6000 |  |  |  |  | 84000
| medium | 20% | 12000 | 12000 | 12000 |  |  |  |  | Misc. site works |  | medium | 20% | [15 empty] | 12000 | 12000 | [15 empty] | 12000 | [5 empty] | 12000 | [6 empty] | 48000
| markup - WW connection available | include if required | [5 empty] | if WW connection is already available on site, no markup |  | Misc. site works |  | markup - WW connection available | include if required | [45 empty] | 0
| At Road | 10% | 6000 | 6000 | 6000 |  |  |  |  | Misc. site works |  | At Road | 10% |  | 6000 | 6000 |  |  | 6000 | 6000 |  | 6000 | 6000 |  |  | 6000 | 6000 | 6000 | 6000 | 6000 |  |  |  | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 |  | 6000 | 6000 |  |  | 6000 | 6000 |  | 6000 | 6000 | 6000 |  |  | 6000 | 6000 |  |  | 168000
| far | 15% | 9000 | 9000 | 9000 |  |  |  |  | Misc. site works |  | far | 15% |  |  |  | 9000 | 9000 |  |  | 9000 |  |  | 9000 | [6 empty] | 9000 | 9000 | [12 empty] | 9000 | 9000 |  |  | 9000 |  |  |  | 9000 | 9000 |  |  |  |  | 99000
| none | 25% | 15000 | 15000 | 15000 |  |  |  |  | Misc. site works |  | none | 25% | 15000 | [18 empty] | 15000 | [25 empty] | 30000
| Civil Subtotal |  | 77000 | 77000 | 77000 |  |  | only include required markups | 10.91% |  |  | Civil Subtotal |  | 75000 | 66000 | 92000 | 74000 | 75000 | 71000 | 66000 | 75000 | 81000 | 71000 | 69000 | 60000 | 72000 | 66000 | 81000 | 107000 | 102000 | 69000 | 75000 | 86000 | 72000 | 66000 | 92000 | 66000 | 71000 | 87000 | 96000 | 90000 | 90000 | 72000 | 71000 | 69000 | 81000 | 92000 | 71000 | 75000 | 71000 | 71000 | 98000 | 75000 | 75000 | 66000 | 71000 | 60000 | 60000 | 3441000
| Civil markup breakdown | [10 empty] | Civil markup breakdown
| Civil subtotal - high markups | site constraints, delivery constraints, no WW connection, tree removal required | 116000 | 116000 | 116000 |  | average Civil subtotal | 76466.6667
| Civil subtotal - medium markups |  | 95000 | 95000 | 95000
| Civil subtotal - low markups |  | 83000 | 83000 | 83000
| Civil subtotal - no markups |  | 60000 | 60000 | 60000
| Electrical | [10 empty] | Electrical
| Electrical allowance (lighting, electrial connections & wiring) - not including any works to bring existing electrical installations in line with current code requirements |  | 30000 | 30000 | 43000 |  |  |  |  | Misc. electrical |  | Electrical allowance (lighting, electrial connections & wiring) - not including any works to bring existing electrical installations in line with current code requirements |  | 30000 | 30000 | 30000 | 43000 | 30000 | 43000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 43000 | 43000 | 30000 | 43000 | 43000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 43000 | 30000 | 30000 | 30000 | 43000 | 30000 | 30000 | 30000 | 1454000
| Electrical Subtotal |  | 30000 | 30000 | 43000 |  |  |  | 7.818% |  |  | Electrical Subtotal |  | 30000 | 30000 | 30000 | 43000 | 30000 | 43000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 43000 | 43000 | 30000 | 43000 | 43000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 43000 | 30000 | 30000 | 30000 | 43000 | 30000 | 30000 | 30000 | 1454000
| I&C | [10 empty] | I&C
| I&C integration allowance |  | 50000 | 50000 | 50000 |  | reference projects | this is equivalent to 2 people working full time for 5 weeks. Could consider pulling this out as a separate task rather than a per-facility estimate |  | N/A |  | I&C integration allowance |  | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 2250000
| New I/O modules |  | 10000 | 10000 | 10000 |  | estimate per workshop discussion | per Karn's estimate. Unclear if this is required at each facility, review with CCC |  | Analyzers, indicators, analytical instruments and misc. instrumentation | [48 empty] | 0
| I&C Subtotal |  | 60000 | 60000 | 60000 |  |  |  | 10.91% |  |  | I&C Subtotal |  | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 50000 | 2250000
| Misc. | [7 empty] | 0% |  |  | Misc.
| Commissioning |  | 12500 | 12500 | 12500 |  |  | per Calista - 100 hours total |  | N/A |  | Commissioning
| SCADA critical spares |  | 5000 | 5000 | 5000 |  | updated per CCC feedback | added per CCC feedback |  | N/A
| Plant Security Allowance (fencing, access control) |  | 15000 | 15000 | 15000 |  |  | fencing, access control. Fencing @$50/m. Estimate 300 m per site. |  | Security |  | Plant Security Allowance (fencing, access control) |  | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 675000
| Misc. Subtotal |  | 33000 | 33000 | 33000 |  |  |  | 6% |  |  | Misc. Subtotal |  | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 15000 | 675000
| Direct Cost Subtotal - Per Facility |  | 443000 | 470000 | 550000 | [6 empty] | Direct Cost Subtotal - Per Facility |  | 440000 | 431000 | 454000 | 516000 | 437000 | 516000 | 428000 | 440000 | 443000 | 436000 | 431000 | 398000 | 437000 | 428000 | 446000 | 472000 | 437000 | 514000 | 517000 | 419000 | 514000 | 468000 | 430000 | 404000 | 406000 | 449000 | 431000 | 455000 | 455000 | 437000 | 436000 | 434000 | 443000 | 454000 | 406000 | 437000 | 409000 | 516000 | 463000 | 437000 | 437000 | 508000 | 406000 | 395000 | 395000 | 20065000
| Direct Cost Estimate - All facilities |  |  |  |  | 20065000
| Markups | [10 empty] | Markups
| Preliminary & General Cost, Mobilization & Demobilization | 30% | 133000 | 141000 | 165000 |  | reference projects | Suggested to decrease to 18% per CCC estimating engineer. However, 30% might be more appropriate for the specialized nature of this work, and given the numerous different contractors and suppliers who will be on site |  |  |  | Preliminary & General Cost, Mobilization & Demobilization |  | 132000 | 130000 | 137000 | 155000 | 132000 | 155000 | 129000 | 132000 | 133000 | 131000 | 130000 | 120000 | 132000 | 129000 | 134000 | 142000 | 132000 | 155000 | 156000 | 126000 | 155000 | 141000 | 129000 | 122000 | 122000 | 135000 | 130000 | 137000 | 137000 | 132000 | 131000 | 131000 | 133000 | 137000 | 122000 | 132000 | 123000 | 155000 | 139000 | 132000 | 132000 | 153000 | 122000 | 119000 | 119000
| Contractor Overhead, Profit and Risk | 15% | 67000 | 71000 | 83000 |  | reference projects |  |  |  |  | Contractor Overhead, Profit and Risk |  | 66000 | 65000 | 69000 | 78000 | 66000 | 78000 | 65000 | 66000 | 67000 | 66000 | 65000 | 60000 | 66000 | 65000 | 67000 | 71000 | 66000 | 78000 | 78000 | 63000 | 78000 | 71000 | 65000 | 61000 | 61000 | 68000 | 65000 | 69000 | 69000 | 66000 | 66000 | 66000 | 67000 | 69000 | 61000 | 66000 | 62000 | 78000 | 70000 | 66000 | 66000 | 77000 | 61000 | 60000 | 60000
| Warranty (Defects Liability Period) | 2% | 9000 | 10000 | 11000 | [6 empty] | Warranty (Defects Liability Period) |  | 9000 | 9000 | 10000 | 11000 | 9000 | 11000 | 9000 | 9000 | 9000 | 9000 | 9000 | 8000 | 9000 | 9000 | 9000 | 10000 | 9000 | 11000 | 11000 | 9000 | 11000 | 10000 | 9000 | 9000 | 9000 | 9000 | 9000 | 10000 | 10000 | 9000 | 9000 | 9000 | 9000 | 10000 | 9000 | 9000 | 9000 | 11000 | 10000 | 9000 | 9000 | 11000 | 9000 | 8000 | 8000
| Construction Subtotal - Per Facility | 47% | 652000 | 692000 | 809000 | [6 empty] | Construction Subtotal - Per Facility |  | 647000 | 635000 | 670000 | 760000 | 644000 | 760000 | 631000 | 647000 | 652000 | 642000 | 635000 | 586000 | 644000 | 631000 | 656000 | 695000 | 644000 | 758000 | 762000 | 617000 | 758000 | 690000 | 633000 | 596000 | 598000 | 661000 | 635000 | 671000 | 671000 | 644000 | 642000 | 640000 | 652000 | 670000 | 598000 | 644000 | 603000 | 760000 | 682000 | 644000 | 644000 | 749000 | 598000 | 582000 | 582000
9498000
| Construction Estimate - All facilities |  |  |  |  | 29563000 | 29563000
| Non Construction Implementation Costs | [10 empty] | Non Construction Implementation Costs
| Permitting & Consents | 2% |  |  |  | 592000 | reference projects |  |  |  |  | Permitting & Consents |  | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000
| Engineering | 13% |  |  |  | 3844000 | reference projects, modified per input from CCC estimating engineer | Based on construction-only contract Additional 1% added to cover the "planning and investigation" stage, as raised by the CCC estimating engineer (approx. $270k) |  |  |  | Engineering |  | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000 | 58000
| Services During Construction (Inspection, Contract Administration) | 7% |  |  |  | 2070000 | CCC estimating practice | Updated to 7% per CCC estimating engineer |  |  |  | Services During Construction (Inspection, Contract Administration) |  | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000 | 31000
| CCC Internal Project Management | 4% |  |  |  | 1183000 | CCC estimating practice | Updated to 4% per CCC estimating engineer
| Documentation Updates (reports, asset management systems, as built drawings, P&IDs, Operating and Maintenance Manuals, field labelling, GIS updates, OEM manuals, SSRMP plans, SOPs, contractor servicing plans, operational and compliance checklists) |  |  |  |  | 675000 | 3 weeks per facility @$125/hr, as noted in CCC feedback | approx 2.6 FTEs. Updated per CCC comment |  |  |  | Documentation Updates (reports, asset management systems, as built drawings, P&IDs, Operating and Maintenance Manuals, field labelling, GIS updates, OEM manuals, SSRMP plans, SOPs, contractor servicing plans, operational and compliance checklists) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SCADA Template development - CCC internal |  |  |  |  | 60000 | estimate per workshop discussion, 12 weeks @$5000/week
| SCADA communications protocols upgrade (transition to DNP3) |  |  |  |  | 1800000 | estimate per workshop discussion | per CCC (Karn), $40k total cost per site, 2-3 weeks of physical work per site |  |  |  | SCADA communications protocols upgrade (transition to DNP3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Chemical/ safety labelling |  |  |  |  | 45000 | per CCC feedback | Pipe labelling, 3 plastic signs per site, one on the gate, building and next to the system. $1K per site
| Training |  |  |  |  | 35000 | ` @$125/hr, as noted in CCC feedback | Upskilling of staff |  |  |  | Training |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Non Construction Implementation Subtotal - All Facilities | 34.85% |  |  |  | 10304000
| Base Estimate - All facilities |  |  |  |  | 39867000
| Contingency | 30% |  |  |  | 11961000 | consistent with CCC estimating practice
| Project Estimate - All facilities | 30% |  |  |  | 51828000
| Escalation | 5% |  |  |  | 6250000 | 28 months @ 5%/year, based on July 2024 midpoint of construction | currently seeing significant escalation in equipment and materials costs. Average increase in the NZ Heavy and civil engineering construction index has been >4%/year since 2019.
| Total Outrun Cost Estimate - All facilities | 5% |  |  |  | 58078000
O&M Cost Estimate
| Item |  |  |  | Hours | Annual Estimate | Full Time Equivalent Staffing | Notes
| Chemical Supply, Delivery and Waste Disposal | [10 empty] | Chemical Supply, Delivery and Waste Disposal
| total annual flow (m3/yr) |  |  |  |  | 58196000 |  | per Michele's email total flow last FY for Christchurch (including Brooklands/Kainga) was 57,112,933 m3. Brooklands/Kainga was 289,376 m3 (included above) Unfortunately we don’t have accurate records for Akaroa WTP – but we can assume 2,000 m3/d x 2 months, and 1,100 m3/d remaining months – round to 580,000 m3. |  |  |  | total annual flow (m3/yr) |  | 919800 | 982872 | 998640 | 2220660 | 1345536 | 2413967.3142 | 1182600 | 1314000 | 1116374.4 | 935568 | 919800 | 748980 | 843588 | 1524240 | 1274580 | 1448028 | 727956 | 3468960 | 2890800 | 1235160 | 3022157.952 | 2628000 | 662256 | 735840 | 735840 | 1387584 | 788400 | 1524240 | 1445400 | 1179972 | 1182600 | 1182600 | 1182600 | 1342908 | 360036 | 1465576.6857 | 315360 | 1752000 | 1432260 | 1156320 | 1314000 | 2018304 | 180860 | 108516 | 580000
| volume of chemical used per year(L/yr) |  |  |  |  | 239000 | [5 empty] | volume of chemical used per year(L/yr) |  | 3765.2656 | 4023.4552 | 4088.0027 | 9090.427 | 5508.0457 | 9881.744 | 4841.0558 | 5378.9509 | 4569.9567 | 3829.813 | 3765.2656 | 3066.002 | 3453.2865 | 6239.583 | 5217.5823 | 5927.6039 | 2979.9388 | 14200.4303 | 11833.6919 | 5056.2138 | 12371.4149 | 10757.9017 | 2710.9912 | 3012.2125 | 3012.2125 | 5680.1721 | 3227.3705 | 6239.583 | 5916.8459 | 4830.2979 | 4841.0558 | 4841.0558 | 4841.0558 | 5497.2878 | 1473.8325 | 5999.4406 | 1290.9482 | 7171.9345 | 5863.0564 | 4733.4768 | 5378.9509 | 8262.0685 | 740.3631 | 444.2178 | 2374.2705
| chemical cost ($/yr), subject to price fluctuations |  |  |  |  | 587000 | [5 empty] | chemical cost ($/yr), subject to price fluctuations |  | 9262.5534 | 9897.6999 | 10056.4865 | 22362.4503 | 13549.7924 | 24309.0902 | 11908.9972 | 13232.2191 | 11242.0934 | 9421.34 | 9262.5534 | 7542.3649 | 8495.0847 | 15349.3742 | 12835.2526 | 14581.9055 | 7330.6494 | 34933.0585 | 29110.8821 | 12438.286 | 30433.6806 | 26464.4382 | 6669.0384 | 7410.0427 | 7410.0427 | 13973.2234 | 7939.3315 | 15349.3742 | 14555.441 | 11882.5328 | 11908.9972 | 11908.9972 | 11908.9972 | 13523.3279 | 3625.628 | 14758.6239 | 3175.7326 | 17642.9588 | 14423.1188 | 11644.3528 | 13232.2191 | 20324.6886 | 1821.2931 | 1092.7759 | 5840.7055
| containers/year |  |  |  |  | 1216 | [5 empty] | containers/year |  | 19 | 21 | 21 | 46 | 28 | 50 | 25 | 27 | 23 | 20 | 19 | 16 | 18 | 32 | 27 | 30 | 15 | 72 | 60 | 26 | 62 | 54 | 14 | 16 | 16 | 29 | 17 | 32 | 30 | 25 | 25 | 25 | 25 | 28 | 8 | 30 | 7 | 36 | 30 | 24 | 27 | 42 | 4 | 3 | 12
| container disposal $/yr |  |  |  |  | 121600 |  | awaiting quote from Envirowaste, placeholder value
| Contract management |  |  |  | 32 | 4000 | per CCC feedback
| PO and invoice processing |  |  |  | 32 | 4000 | per CCC feedback
| Chemical Supply Subtotal |  |  |  |  | 716600
Compliance Management, Maintenance and Inspection
| Breakdown | Annual Frequency | Duration | No. Sites | Total Hours | Annual Cost | FTEs | per Code of practice. Assumes staff are already travelling to site weekly
| Daily changes in the volume/mass of fluoride chemical consumed in the process must be recorded and used as an additional check of the online measurements | 12 | 1 | 1 | 12 | 1500 | 0.0057692 | monthly review
| Grab samples should be analysed at least weekly to check the calibration of the on-line analyser | 52 | 0.5 | 45 | 1170 | 146250 | 0.5625 | weekly sampling
| fluoride level in the treated water leaving the plant is analysed once a week, by a laboratory recognised by the Ministry of Health. To be integrated in the Water Safety Plan | 52 | 0.5 | 45 | 1170 | 146250 | 0.5625 | weekly sampling
[6 empty] | 234000 |  | additional cost for analysis to be confirmed. Approx. $100/sample assumed
| After-hours response to alarms | 24 | 4 | 1 | 96 | 12000 | 0.046154
| Investigate and rectify any discrepancies of 0.15 mg/L or more between the monitoring results and the online monitoring and daily chemical volume checks | 2 | 40 | 1 | 80 | 10000 | 0.038462
| Annual testing of shutdown systems | 1 | 2 | 45 | 90 | 11250 | 0.043269
| Annual raw water fluoride testing |  |  |  | 0 | 0 |  | (already on going)
| Monthly metering pump calibration | 12 | 0.5 | 45 | 270 | 33750 | 0.12981
| Analyzer calibration (required monthly per Taumata Arowai) | 12 | 0.5 | 45 | 270 | 33750 | 0.12981
| Receive chemical shipments and transfer to bulk chemical tank | 12 | 2 | 45 | 1080 | 135000 | 0.51923
| Monthly inspections and preventative maintenance | 12 | 3 | 45 | 1620 | 202500 | 0.77885
| Reactive Maintenance | 1 | 8 | 23 | 184 | 23000 | 0.088462 | 1 event per year at 50% of the facilities
| SCADA Management | 12 | 2 | 45 | 1080 | 135000 | 0.51923 | 2 hours per site per month.
| Training/review to maintain competencies in the management and operation of the fluoridation systems | 1 | 8 | 5 | 40 | 5000 | 0.019231
| Recordkeeping (training records, chemical analysis, calibration, alarm testing, surveillance monitoring, etc) | 1 | 1 | 45 | 45 | 5625 | 0.021635
| Compliance Management, Maintenance and Inspection Subtotal |  |  |  | 7207 | 1135000 | 3.4649 | approximately 3 full time staff, additional activities only (not including travel time to sites)
| Total O&M Cost Estimate - All facilities |  |  |  | 7207 | 1851600 | 3.4649
Renewal Budget
| Asset | Replacement Value | Replacement Value with markups (35% from direct cost to construction estimate, further 25% for project costs) | midlife intervention frequency (years) | Useful life (years) | midlife intervention cost | Spend Years 1-5 | Spend Years 6-10 | Spend Years 11-15 | Spend Years 16-20
| Liquid chemical system | 1948000 | 3287250 |  | 10 |  |  | 3287250 |  | 3287250
| Appurtenances of the system (e.g. piping, tanks) | 2793300 | 4713693.75 |  | 10 |  |  | 4713693.75 |  | 4713693.75
| Health and safety equipment | 180000 | 303750 |  | 10 |  |  | 303750 |  | 303750
| Scrubber media for a passive scrubber | 45000 | 75937.5 |  | 5 |  | 75937.5 | 75937.5 | 75937.5 | 75937.5
| Air handling units and misc. building mechanical | 675000 | 1139062.5 | 15 | 25 | 341718.75 |  |  | 341718.75
| Analyzers, indicators, analytical instruments and misc. instrumentation | 2272000 | 3834000 |  | 10 |  |  | 3834000 |  | 3834000
| Misc. electrical | 1454000 | 2453625 |  | 30
| Misc. site works | 3441000 | 5806687.5 |  | 40
| Misc. light structural | 1432000 | 2416500 | 10 | 40 | 483300 |  | 483300 |  | 483300
| Security | 675000 | 1139062.5 |  | 8 |  |  | 1139062.5 |  | 1139062.5
| Signage | 45000 | 75937.5 |  | 20 |  |  |  |  | 75937.5
|  | 14960300 | 25245506.25 |  |  |  | 75937.5 | 13836993.75 | 417656.25 | 13912931.25
| Annualized State of Good Repair Cost | Annualized Replacement Cost | No. Midlife interventions in useful life | Annualized Midlife intervention Cost | Total Annualized Cost
| Liquid chemical system | 194800 |  | 0 | 194800
| Appurtenances of the system (e.g. piping, tanks) | 279330 |  | 0 | 279330
| Health and safety equipment | 18000 |  | 0 | 18000
| Scrubber media for a passive scrubber | 9000 |  | 0 | 9000
| Air handling units and misc. building mechanical | 27000 | 1 | 13668.75 | 40668.75
| Analyzers, indicators, analytical instruments and misc. instrumentation | 227200 |  | 0 | 227200
| Misc. electrical | 48466.6667 |  | 0 | 48466.6667
| Misc. site works | 86025 |  | 0 | 86025
| Misc. light structural | 35800 | 3 | 36247.5 | 72047.5
| Security | 84375 |  | 0 | 84375
| Signage | 2250 |  | 0 | 2250
1062162.9167
Note on BE146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: updated per MIchele's email March 7, 2022
Note on BF146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: updated per MIchele's email March 7, 2022
Note on BG146: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: updated per MIchele's email March 7, 2022

## Schedule
Preliminary Schedule Estimate
Task | Duration | Notes | April | May | June | July | August | September | October | November | December | January | February | March | April | May | June | July | August | September | October | November | December | January | February | March | April | May | June | July | August | September | October | November | December | January | February | March | April | May | June | July | August | September | October | November | December | January | February | March | April | May | June | July | August | September | October | November | December
|  |  | Year 1 | [8 empty] | Year 2 | [11 empty] | Year 3 | [11 empty] | Year 4 | [11 empty] | Year 5
Implementation Planning
Preliminary Designs of selected facilities and updated costing | 4 months | Apr. - Jul. 2022 | bar: April to July
Priority Facilities |  | assume 15 facilities per tract
Detailed Design | 7 months | depends on how many we want to delivery in the "priority" tract | bar: October to April
Tendering Period | 4 months | includes prepration, issue for tender, tender period, evaluation and award | bar: May to August
Mobilization | 1 month | Wait until fall to start, as construction is constrained in the summer | bar: September
Civil and structural works | 6 weeks | stagger to start 5 facilities at a time, in 3 waves 1 month apart | bar: October to January
Equipment lead time | 6 months | from contract award, allowing an additional 4 weeks for the contractor to finalize quotes and place orders. Schedule could be compressed by pre-purchasing equipment with long lead time | bar: October to March
Equipment installation, startup and commissioning | 6 weeks | bar: April to July
Warranty Period | 1 year | bar: June to August
Secondary Facilities |  | assume 15 facilities
Detailed Design | 4 months | standardized design, documenting differences | bar: May to August
Tendering | 4 months | bar: September to December
Mobilization | 1 month | bar: January
Civil and structural works | 6 weeks | bar: February to May
Equipment lead time | 6 months | from contract award, allowing an additional 4 weeks for the contractor to finalize quotes and place orders. | bar: February to July
Equipment installation, startup and commissioning | 6 weeks | bar: August to November
Warranty Period | 1 year | bar: October to December
Tertiary Facilities |  | assume 15 facilities
Detailed Design | 4 months | standardized design, documenting differences | bar: May to August
Tendering | 4 months | bar: September to December
Mobilization | 1 month | bar: January
Civil and structural works | 6 weeks | bar: February to May
Equipment lead time | 6 months | from contract award, allowing an additional 4 weeks for the contractor to finalize quotes and place orders. | bar: February to July
Equipment installation, startup and commissioning | 6 weeks | bar: August to November
Warranty Period | 1 year | bar: October to December

## Inflation Review
Inflation Estimate
Heavy and civil engineering construction index
| SQNEE1200 | Date | Annual % increase | Quarterly % increase
| 1181 | Dec-19
| 1182 | Mar-20 |  | 0.08467%
| 1166 | Jun-20 |  | -1.354%
| 1181 | Sep-20 |  | 1.286%
| 1182 | Dec-20 | 0.08467% | 0.08467%
| 1198 | Mar-21 | 1.354% | 1.354%
| 1223 | Jun-21 | 4.889% | 2.087%
| 1253 | Sep-21 | 6.097% | 2.453%
| 1288 | Dec-21 | 8.968% | 2.793%
|  | Average | 4.278% | 1.099%

## Chemical Sizing
Chemical System Sizing
Parameter | Small System Range |  | Medium System Range |  |  | Large System Range |  | Units | Notes
Max Flow | 7.2 | 2.112 | 13.92 | 7.68 |  | 31.68 | 16.008 | MLD
| 300 | 88 | 580 | 320 |  | 1320 | 667 | m3/hr
average flow | 2.4 | 0.704 | 4.64 | 2.56 |  | 10.56 | 5.336 | MLD | Per Michele: Peak demand is 3x more than average demand
minimum Flow | 0.72 | 0.2112 | 1.392 | 0.768 |  | 3.168 | 1.6008 | MLD | assume 10% of max flow
Hydrofluorosilicic Acid
Parameter | Small System Range |  | Medium System Range |  |  | Large System Range |  | Units | Notes
No. Application points (duty) | 1 | 1 | 1 | 1 |  | 1 | 1
No. Application points (total) | 1 | 1 | 1 | 1 |  | 1 | 1
Chemical storage time requirement | 14 | 14 | 14 | 14 |  | 14 | 14 | days | per client meeting, 2-4 weeks supply.
Chemical storage calculation basis | Average Flow, Average Dose | Average Flow, Average Dose | Average Flow, Average Dose | Average Flow, Average Dose |  | Average Flow, Average Dose | Average Flow, Average Dose
Minimum bulk storage volume required | 0.13754 | 0.035863 | 0.26592 | 0.13041 |  | 0.60519 | 0.30581 | m3
No. bulk Chemical Storage tanks | 1 | 1 | 2 | 2 |  | 1 | 1
Individual bulk storage tank volume | 0.2 | 0.2 | 0.2 | 0.2 |  | 1 | 1 | m3 | IBC at 1.14 m3. Consider using 2 x 0.2 m3 drums, or smaller carboys
Total Storage Volume | 0.2 | 0.2 | 0.4 | 0.4 |  | 1 | 1 | m3
No. active metering pumps | 1 | 1 | 1 | 1 |  | 1 | 1 |  | only one pump needed for turn down 1:100
no. standby metering pumps | 1 | 1 | 1 | 1 |  | 1 | 1
Dose - max | 1 | 1 | 1 | 1 |  | 1 | 1 | mg/L
Dose - average | 0.9 | 0.8 | 0.9 | 0.8 |  | 0.9 | 0.9 | mg/L | assume no background F, conservative dosing
Dose - min | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.4 | 0.4 | mg/L
% active chemical | 18.17% | 18.17% | 18.17% | 18.17% |  | 18.17% | 18.17% | % w/w | based on 23% concentration with 79% available fluoride
specific gravity | 1.21 | 1.21 | 1.21 | 1.21 |  | 1.21 | 1.21
active chemical concentration | 219.857 | 219.857 | 219.857 | 219.857 |  | 219.857 | 219.857 | kg/m3
| 0.21986 | 0.21986 | 0.21986 | 0.21986 |  | 0.21986 | 0.21986 | kg/L
Max dose "dry" chemical application | 7.2 | 2.112 | 13.92 | 7.68 |  | 31.68 | 16.008 | kg/d
Max flow at feed concentration | 1.3645 | 0.40026 | 2.6381 | 1.4555 |  | 6.0039 | 3.0338 | L/h | per duty application point
days storage at avg. flow, avg. dose | 20.3571 | 78.0742 | 21.0591 | 42.9408 |  | 23.1331 | 45.7807 | days | HFA is stable for 3 months without issue
days storage at max. flow, avg. dose | 6.7857 | 7.6339 | 13.5714 | 15.2678 |  | 7.711 | 7.711 | days
days storage at max. flow, max. dose | 6.1071 | 6.1071 | 12.2143 | 12.2143 |  | 6.9399 | 6.9399 | days
No. Day Tanks | 1 | 1 | 1 | 1 |  | 1 | 1
No. Hours in Operation per Day | 24 | 24 | 24 | 24 |  | 24 | 24 | hours/ day
Day Tank Volume required for Max. Flow, Max Dose | 32.7486 | 9.6062 | 63.3139 | 34.9318 |  | 144.0937 | 72.811 | L
No. Day Tank Transfer Pumps | 1 | 1 | 1 | 1 | 1 | 1 | 1
No. Carrier Water Pumps | 1 | 1 | 1 | 1 |  | 1 | 1
Dilution ratio (1:X) | 100 | 100 | 100 | 100 |  | 100 | 100
carrier water flow rate | 136.4523 | 40.026 | 263.8078 | 145.5492 |  | 600.3903 | 303.379 | L/h | based on max flow at feed concentration
| 0.037903 | 0.011118 | 0.07328 | 0.04043 |  | 0.16678 | 0.084272 | L/s

## PS List with Markup Factors
CHRISTCHURCH PUMP STATION LIST (February 2022)
| Comments | [18 empty] | Urban? Proximity of consumers? | Assessment of accessway and space for turning larger vehicles. Minor - need to reverse out |  | Building expansion or new stand-alone building required | assume 4 x 4 m, review per previous report on poential UV equipment locations | On site, on road (either side), far (down an accessway with residential housing in between), none visible on previous site footprint assessment, or Cantebury Maps. | Carters and a few(5-10) other stations (Eastern side) have vacuum ww mains systems that would require batching | Yes (likely) /no |  |  | 30 pipe diameters between metering chamber (point of injection) and sampling point (before 1st diversion)
PS# | Water Supply Zone | PS Name | Water Supply | PS Number | Include / Exclude | PS Type | Description | Suction Tank | Suction Tank Volume (m3) | No. Wells | No. Surface Pumps | Pump Size (m3/hr/pump) | Max historic Q (m3/hr) | PS Capacity Now (m3/hr) | PS Capacity Future (m3/hr) | CCC Notes | PS Capacity Now (ML/d) | PS Capacity Future (ML/d) | Part of City Care Assessment | Site Setting | Delivery Constraints | Building expansion required | Standalone Building Required (Yes/No) | Overall Site Constraints | WW Connection On Site | Vacuum Wastewater? | Tree Removal Required | Distance from metering chamber to point of 1st diversion (m) | Pipe Diameter (mm) | Mixer Required | Eyewash Station Required | Site Comments | Notes
1 | North West | Thompsons | Christchurch | PS1078 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 377 | 350 | 350 |  | 8.4 | 8.4 |  | Urban | None | Yes | No | None | None | Yes | No | 9 | 300 | Yes | Yes | There is space on site for building expansion, good access Per Karn's comment on Thursday, this is "tight, landwise" | Close for mixer
2 | North West | Avonhead | Christchurch | PS1069 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 374 | 374 | 374 |  | 8.976 | 8.976 |  | Urban | None | Yes | No | None | At Road | Yes | No | 7.4 | 375 | Yes | Yes | Sufficient space for building expansion. Good site access.
3 | North West | Belfast | Christchurch | PS1070 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 2 | 1 | 200 | 261 | 380 | 380 | changes made to station to achieve higher max | 9.12 | 9.12 |  | Urban | Minor | Yes | Yes | Medium | At Road | No | Yes | 27 | 300 | No | Yes | Tight accessway, no turning circle present, reversing only. Building expansion will block access to site. New building required.
4 | North West | Burnside | Christchurch | PS1071 | include | 1 | submersible pumped into mains | û |  | 6 | n/a |  | 779 | 845 | 845 |  | 20.28 | 20.28 |  | Public space | None | Yes | No | None | Far | No | Yes | 18 | 300 | No | Yes | Located within public park, plenty of space, consider extra precaution due to public access. | Complicated piping, check
5 | North West | Crosbie | Christchurch | PS1072 | include | 1 | submersible pumped into mains | û |  | 3 | n/a |  | 512 | 512 | 512 |  | 12.288 | 12.288 |  | Urban | Minor | Yes | Yes | None | Far | No | No | See note | 300 | No | Yes | Space available on site. Building expansion constrained, will require detached building. | Meter looks to be after a mains offtake. One bore goes straight to network and has a separate chlorine installation from the other two bores, slightly complicated for contact time. Therre is time before network but needs to be relocated prior to take off
6 | North West | Farrington | Christchurch | PS1073 | include | 1 | submersible pumped into mains | û |  | 5 | n/a |  | 918.5568 | 918.5568 | 918.5568 |  | 22.0454 | 22.0454 |  | Urban | None | Yes | No | None | At Road | No | Yes | 7 | 300 | Yes | Yes | Tight accessway, sufficient space onsite adjacent to existing building for expansion.
7 | North West | Grampian | Christchurch | PS1074 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 160/160/130 | 430 | 430 | 450 |  | 10.32 | 10.8 | Yes | Urban | None | Yes | Yes | None | At Road | No | No | 14 | 225 | No | Yes | Expansion space present but not near existing building so new building required. Space near the back of site.
8 | North West | Jeffreys | Christchurch | PS1076 | include | 2 | suction tank / surface pumped into mains | Yes | 450 | 4 | 2 | 140/140 250/250 future | 246 | 246 | 500 | suction tank being constructed / pumps upgraded | 5.904 | 12 |  | Urban | Minor | Yes | No | None | Far | No | No | 15 | 300 | No | Yes | Room for expansion on building. Small turning circle and narrow long access way
9 | North West | Redwood | Christchurch | PS1077 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 535 | 0 | 424.8 | work underway to renew wells | 0 | 10.1952 |  | Urban | None | Yes | Yes | Medium | At Road | No | No | 8 | 200 | No | Yes | Very small site. Will require removal of trees for additional building. Only room to drive in and back out of site off busy road. | Close for mixer
10 | North West | Wrights | Christchurch | PS1080 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 381 | 356 | 356 |  | 8.544 | 8.544 |  | Commercial | None | Yes | No | None | At Road | No | Yes | 8 | 250 | Yes | Yes | Large site, lots of scape, large area for turning etc. | No meter present but close connection to roadside
11 | North West | Gardiners | Christchurch | PS1125 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 2 | 2 | 180/180 | 350 | 350 | 350 |  | 8.4 | 8.4 |  | Rural | None | Yes | No | None | Far | No | No | >40 | assume 250 (PE355) | No | Yes | Large site, good delivery options, room for expansion
12 | Rawhiti | Aston | Christchurch | PS1004 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 169/169 | 285 | 285 | 285 |  | 6.84 | 6.84 | Yes | Urban | None | Yes | No | None | On Site | Yes | No | 6 | 200-300 | Yes | Yes | Good reversing back for delivery, potential room on site for building expansion
13 | Rawhiti | Effingham | Christchurch | PS1010 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225 | 445 | 321 | 321 |  | 7.704 | 7.704 |  | Urban | Minor | Yes | No | None | At Road | Yes | No | 2 | 200 | Yes | Yes | Small access only to the front of the building, new building expansion round the back, good space.
14 | Rawhiti | Keyes | Christchurch | PS1119 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 180/200/200 | 593 | 580 | 580 |  | 13.92 | 13.92 | Yes | Urban | None | Yes | No | None | At Road | Yes | No | Cannot see meter | 300 | No | Yes | Good access to site, should be space for building expansion, if not, plenty of room for new building. | Cannot see meter but long distance to mains on road, safely say no mixer required.
15 | Rawhiti | Lake Terrace | Christchurch | PS1023 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 2 | 260/225 | 829 | 485 | 485 |  | 11.64 | 11.64 |  | Urban | None | Yes | Yes | Medium | At Road | Yes | No | 1 | 250 | Yes | Yes | Good delivery, constrained site with not much room for building expansion but should be sufficient for site expansion. | division immediately upstream of meter but does not see consumer for over 30 m on diversions
16 | Rawhiti | Carters | Christchurch | PS1008 | include | 2 | suction tank / surface pumped into mains | Yes |  | 4 | 2 | 225/225=450 | 580 | 551 | 551 |  | 13.224 | 13.224 | Yes | Urban | Medium | Yes | N/A | High | At Road | Yes | Yes | 5.5 | 250 | Yes | Yes | Very small site. No room for building or site expansion. Poor delivery access. Very constrained site.
17 | Rawhiti | Estuary | Christchurch | PS1012 | include | 2 | suction tank / surface pumped into mains | Yes |  | 1 | 2 | 182/108=290 | 319 | 277 | 277 |  | 6.648 | 6.648 |  | Urban | Medium | Yes | N/A | High | At Road | Yes | No | 15 | 200 | No | Yes | Very small site. No room for building or site expansion. Poor delivery access. Very constrained site.
18 | West | Sockburn | Christchurch | PS1109 | include | 2 | suction tank / surface pumped into mains | Yes | 4500 | 6 | 2 | 792/792 = 1584 | 1312 | 1320 | 1320 | another pump as standby - well capacity used for PS max | 31.68 | 31.68 |  | Commercial | None | Yes | No | None | Far | No | No | 12 | 450 | Yes | Yes | Good site. Plenty of space. Easy delivery. Lots of room for building expansion. | Technically long pipelines after 1st diversion before consumers could mean no mixer but 2 no. analysers?
19 | West | Denton | Christchurch | PS1099 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 5 | 2 | 900/900 = 1,800 | 1099 | 1100 | 1100 | another pump as standby - well capacity used for PS max | 26.4 | 26.4 |  | Semi-urban | Minor | Yes | No | None | Far | No | No | Cannot see meter | 375 | No | Yes | Good space on site for building expansion. Slightly difficult access with long thin access road. No turning circle etc. | Cannot see meter but long distance to mains on road, safely say no mixer required.
20 | West | Wilmers | Christchurch | PS1117 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 2 | 3 | 400/780/780 = 1,960 | 1254 | 470 | 470 | well capacity used for PS max - will be expanded in future | 11.28 | 11.28 |  | Urban | None | No | Yes | Minor | None | No | Yes | Cannot see meter | 500 | Yes | Yes | Suitable space for site expansion but will be difficult for a building expansion potentially. Difficult access for chemical delivery. | 18 m post pumps but no sign of meter chmaber for dosing? Probably doesn’t need mixer check
21 | West | Dunbars | Christchurch | PS1102 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 4 | 2 | 900/900 = 1,800 | 1433 | 1149.984 | 1149.984 | another pump as standby - well capacity used for PS max | 27.5996 | 27.5996 |  | Urban | Minor | Yes | No | None | At Road | No | No | 18 | 450 | No | Yes | Slightly tight delivery circle, plenty of space for building expansion.
22 | Central | Main Pumps WS | Christchurch | PS1024 | include | 2 | suction tank / surface pumped into mains | Yes | 1085 | 6 | 3 | 225/450/500=1,175 | 1138 | 1000 | 1000 |  | 24 | 24 |  | Urban | None | No | No | N/A | At Road | No | No | Cannot see meter | 300 | No | Yes | Cannot find | Cannot see meter but long distance to mains on road, check
23 | Central | Addington | Christchurch | PS1001 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 260 | 252 | 252 |  | 6.048 | 6.048 |  | Urban | Minor | Yes | No | Medium | At Road | No | Yes | 5 | 300 | Yes | Yes | Small site. Minimal delivery space for vehicles. Small area for building expansion which may be suitable. Difficult satellite imagery to tell how much space is available.
24 | Central | Aldwins | Christchurch | PS1002 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 230/230=460 | 287 | 280 | 280 | max PS capacity before becoming airlocked | 6.72 | 6.72 | Yes | Urban | None | Yes | No | None | At Road | No | No | 7.7 | 300 | Yes | Yes | Good site. Plenty of space. Wide delivery access. Simple building expansion.
25 | Central | Blighs | Christchurch | PS1007 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 2 | 1 | 225 | 286 | 280 | 280 | 1 of wells being developed | 6.72 | 6.72 |  | Urban | None | Yes | No | None | At Road | No | Yes | 20 | 200 | No | Yes | Compact site. Suitable space for building expansion. Delivery is reverse in and back out.
26 | Central | Grassmere | Christchurch | PS1014 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 528 | 528 | 528 |  | 12.672 | 12.672 |  | Urban | Minor | Yes | No | Medium | At Road | No | No | 9 | 200 | No | Yes | Small space approx. 12-14 m2 for building expansion. Separate building would be difficult on site if this doesn’t work. Delivery is minor constraint with little space.
27 | Central | Hillmorton | Christchurch | PS1016 | include | 2 | suction tank / surface pumped into mains | Yes | 310 | 2 | 1 | 225 | 313 | 300 | 300 |  | 7.2 | 7.2 |  | Urban | Minor | Yes | Yes | High | At Road | No | No | 22 | 300 | No | Yes | Very small site. Constrained for building expansion near current pump room. Small delivery bay present.
28 | Central | Hills | Christchurch | PS1017 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 622 | 580 | 580 |  | 13.92 | 13.92 |  | Urban | None | Yes | Minor | High | At Road | No | No | 5 | 200-300 | Yes | Yes | Building expansion will be tight, there is space around site however. Could remove scrub to make space on building. Small delivery bay present
29 | Central | Mays | Christchurch | PS1026 | include | 2 | suction tank / surface pumped into mains | Yes | 350 | 3 | 2 | 225/225=450 | 551 | 225 | 550 | 3'rd well being developed | 5.4 | 13.2 |  | Urban | Minor | Yes | Yes | High | On Site | No | No | 6 | 300 | Yes | Yes | Very constrained site. Small delivery access road. Building expansion very limited but some space elsewhere on site.
30 | Central | Montreal | Christchurch | PS1027 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 449 | 449 | 449 |  | 10.776 | 10.776 |  | Urban | None | Yes | No | Minor | At Road | No | No | Cannot see meter | 200 | Yes | Yes | Space around the side of the building for expansion. Construction is narrow corridor of space could be difficult. | Cannot see meter but very close to roadsite and connections. Expeceted less than 5 metres so mixer
31 | Central | Spreydon | Christchurch | PS1030 | include | 2 | suction tank / surface pumped into mains | Yes |  | 5 | 2 | 225/225=450 | 455 | 225 | 450 | 2 wells being developed | 5.4 | 10.8 |  | Urban | None | Yes | No | None | At Road | No | Yes | Cannot see meter | 200 | Yes | Yes | Delivery space on the smaller side. Plenty of space for building expansion etc. | Cannot see meter but very close to roadsite and connections. Expeceted less than 6 metres so mixer
32 | Central | Sydenham | Christchurch | PS1031 | include | 2 | suction tank / surface pumped into mains | Yes | 315 | 4 | 2 | 225/225=450 | 487 | 450 | 450 | suction tank being renewed | 10.8 | 10.8 |  | Commercial | None | Yes | No | None | Far | No | No | 3 | 200 | Yes | Yes | Commercial site with plenty of space for both delivery and building expansion. | Technically long pipelines after 1st diversion before consumers could mean no mixer but 2 no. analysers?
33 | Central | Trafalgar | Christchurch | PS1035 | include | 2 | suction tank / surface pumped into mains | Yes | 250 | 3 | 2 | 225/225=450 | 510 | 450 | 450 |  | 10.8 | 10.8 |  | Urban | Medium | Yes | No | None | Far | No | No | >50 | 250 | No | Yes | Site with plenty of space. Only constraint is very thin access road by past residential propoerties. | Very long accessway before connection
34 | Central | Worcester | Christchurch | PS1037 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225=450 | 511 | 511 | 511 |  | 12.264 | 12.264 |  | Urban | Minor | Yes | Yes | Medium | At Road | No | Yes | Cannot see meter | 375 | No | Yes | Thin access site passing residential properties. Any building expansion will block access to site unless trees etc are removed at the back of the site. | Cannot see meter but minimum 30 m to main on road (not 1st diversion)
35 | Central | Tanner | Christchurch | PS1095 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 137 | 137 | 137 |  | 3.288 | 3.288 |  | Urban | None | Yes | No | None | At Road | No | Yes | >50 (offsite) | 200 | No | Yes | Small building, large site for expansion. Huge space for delivery. | Site pipe to retic has no consumers till further down street so could be worth installating mixer incase new connections earlier in line.
36 | Riccarton | Picton | Christchurch | PS1088 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 3 | 2 | 220/220 +190 = 630 | 557.6776 | 557.6776 | 557.6776 |  | 13.3843 | 13.3843 |  | Urban | Minor | Yes | No | None | Far | No | No | >50 | 300 | No | Yes | Tight access with small turning circle near children playground. Space for building expansion with plenty of room. | Note that we have sand filter post metering chamber
37 | Riccarton | Tara | Christchurch | PS1089 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 249 | 120 | 120 |  | 2.88 | 2.88 |  | Urban | None | Yes | No | None | At Road | No | Yes | 5 | 200 | Yes | Yes | Not sure where the current delivery is located. Minimal access on satelliate. Open site with extensive room for expansion as required. | Not sure where dosing location is. Currently measured from M chmaber but Cl tank is closer to bore. If dosing is closer to bore, then no mixer required.
38 | Ferrymead | St Johns | Christchurch | PS1063 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 3 | 2 | 225/450=675 | 634 | 666.6667 | 666.6667 | max PS capacity = well consent | 16 | 16 |  | Urban | None | Yes | No | None | At Road | No | Yes | <5 | 300 | Yes | Yes | There is space on site for building expansion and delivery is adjacent to the road curb.
39 | Ferrymead | Woolston | Christchurch | PS1065 | include | 2 | suction tank / surface pumped into mains | Yes | 400 | 3 | 3 | 250/250/250=750 | 639 | 545 | 545 |  | 13.08 | 13.08 | Yes | Urban | Medium | Yes | No | Medium | At Road | No | Yes | Cannot see meter | 250 | Yes | Yes | There is a small section of small to the front of the building which is the only section available. Approx 10 m2 of space. | Cannot see meter but very close to 1st diversion connections. Expeceted less than 5 metres so mixer
40 | Parklands | Marshlands | Christchurch | PS1084 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 220/220 = 440 | 412 | 440 | 440 |  | 10.56 | 10.56 |  | Urban | Minor | Yes | No | None | Far | No | No | 19 | 300 | No | Yes | There is space on site for building expansion and delivery to the front of the building down reasonably tight access road. | Note that we have sand filter post metering chamber
41 | Parklands | Parklands | Christchurch | PS1085 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 3 | 164/355/200 = 719 | 499 | 500 | 500 |  | 12 | 12 |  | Urban | Minor | Yes | No | None | Far | No | No | >50 | 300 | No | Yes | There is space on site for building expansion and delivery down reasonably tight access road.
42 | Parklands | Prestons | Christchurch | PS1123 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 4 | 3 | 200/200/200 = 600 | 768 | 768 | 768 |  | 18.432 | 18.432 |  | Urban | None | Yes | No | None | At Road | No | No | Cannot see meter | 300 | No | Yes | Good size site. Plenty of space for building expansion and delivery to site. No contraints. | No meter on file but good distance to main on road. No mixer
43 | Kainga/Brooklands | Brooklands | Brooklands / Kainga | PS1066 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 142 | 180 | 180 |  | 4.32 | 4.32 |  | Rural | None | Yes | No | None | At Road | No | Yes | 25 | 200 | No | Yes | No issue with space or delivery to site. Good wide access and plnety of space to expand.
44 | Kainga/Brooklands | Kainga | Brooklands / Kainga | PS1067 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 112 | 108 | 108 |  | 2.592 | 2.592 |  | Urban | None | Yes | No | None | On Site | No | No | >30 | 200 | No | Yes | No issue with space or delivery to site. Good wide access and plnety of space to expand.
45 |  | Akaroa L’Aube Hill WTP | Akaroa | TP | include | [8 empty] | 87.5 | 87.5 | comprises two membrane skids with minimum capacity of 400 m3/day and maximum 2,100 m3/day. | 2.1 | 2.1 |  | Rural | None | Yes | No | No | On Site | No | No |  |  | No | Yes | Cannot locate | added per email from Michele McDonald
[6 empty] | 1 | submersible pumped into mains
[6 empty] | 2 | suction tank / surface pumped into mains
[6 empty] | 3 | submersible + artesian/surface pumped into mains
[6 empty] | 4 | artesian/surface pumped into mains
Note on U3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Located with urban area or semi-rural. close to consumers etc.
Note on V3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assessment of accessway and space for turning larger vehicles.
Note on W3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there space for building expansion or will a new detached building be required
Note on X3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there space for building expansion or will a new detached building be required
Note on Y3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is the current site boundary suitable for additional 4x4 area anywhere
Note on AG25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: have a look at the water supply overview schematic. Looks like it's between Thorrington and Palatine

## Vendor Quotes (hidden)
Conceptual
FLUORIDE DOSING
Design Element | Units | Cost
ProMinent 250L Chemical Tank |  | 1892 | ChemFeed
1000 L Self-bunded Chemical Storage Tank |  | 10543.9
Self bunded HDPE chemical storage tank | 1
CAD drawings for Chemical Tanks | 1
Chemical tank HSNO engineering | 1
Tank HSNO label | 1
Tank Accessories
Ultrasonic level indicator | 1 | 968
Ultrasnoic level switch | 1 | 408.91
Tanker loading station for engineered tanks | 1 | 2950
Leak detection switch | 1 | 287
Dosing Skid |  | 21392.3
Labour | 16
Dosing cabinet 1600w 1950 h 600 d | 1
Day tank | 1
Day tank ultra sonic level transmitter | 1
Transfer pump - DFAa 14 L/hr 0.18 kW | 1
Gamma x dosing pump, 3.6L/HR16Bar, PVT Head, Bleed Valve no springs,running & fault relay, 4-20mA input, 2m Control Cable | 1
Motorised valve | 1
Pulsation dampner | 1
SCH80 15mm PVC pipework and valves
Pressure guage
DN15 PVC SCH80
Consumables
FLUORIDE DOSING | [6 empty] | Notes
Variables | [5 empty] | Assumptions
Population Served |  | 10k-20k | 20k-30k | 50k-100k | 100k-150k
Capacity (m3/day) |  | 6000 | 15000 | 30000 | 45000 | 300 L/d/p
m3/hr |  | 250 | 625 | 1250 | 1875
Equipment including Installation
Analyser |  | 17500 | 17500 | 17500 | 17500
Safety shower |  | 7000 | 7000 | 7000 | 7000
HAZOP |  | 7500 | 7500 | 7500 | 7500
Storage tank capacity (l) |  | 600 | 1500 | 3200 | 6500 |  | approx. cost for 1000 L tank
Storage tank |  | 7500 | 10000 | 12500 | 15000 | 30 days | 8611.1111
Day tank capacity |  | 20 | 50 | 100 | 200
Day tank |  | 1500 | 3000 | 5000 | 8000
Transfer pump |  | 5000 | 7500 | 10000 | 12500
Dosing pump/pipework |  | 15000 | 29000 | 43000 | 58000
Flowmeter |  | 15000 | 17500 | 20000 | 22500
subtotal |  | 76000 | 99000 | 122500 | 148000
Installation and commissioning |  | 43000 | 50000 | 58000 | 65000 |  | 44-56% of capital
Electrical and automation |  | 36000 | 40000 | 43000 | 46000 |  | 31-47% of capital
Total |  | 155000 | 189000 | 224000 | 259000
Exclusions
Freight to site
Civil works
Building upgrades
Bunding
SCADA upgrade and integration
On-line monitoring operational costs
HFA supply
HFA unloading system
Operator costs
Maintenance
Injection point pipework
Duty dosing pump only
Ventilation
Waste disposal
Plant security
Heating (HFA freezes at 0°C)
HASNO compliance
Power connection
FLUORIDE ANALYSER
Fluoride Analyser
AMI ISE Universal for AC Operation | 1 | 6866 | SWAN Analytical
Fluoride Sensor | 1 | 2967
Sensor reference fluid with electrolyte | 1 | 550
Sensor Flow Delta (optional) | 1 | 800
11183
AFM631 Sensor | 1 | 11445 | ABB
Calibration standard level sensor | 1 | 333
SD storage | 1 | 18
Caliration certificate | 1 | 218
Reagent tray | 1 | 366
Annual maintenance kit | 1 | 291
12671
CHEMICAL DELIVERY
Chemical Delivery | $/L (exc) | 2.46 | Ixom

## PS Pivot
Include / Exclude | include
Count of PS Name | Column Labels
Row Labels | artesian/surface pumped into mains | submersible + artesian/surface pumped into mains | submersible pumped into mains | suction tank / surface pumped into mains | (blank) | Grand Total
85-300 m3/hr | 2 |  | 5 | 3 | 1 | 11
300-588 m3/hr | 4 | 2 | 6 | 14 |  | 26
666-1320 m3/hr |  |  | 2 | 6 |  | 8
Grand Total | 6 | 2 | 13 | 23 | 1 | 45

## Original PS List (hidden)
CHRISTCHURCH PUMP STATION LIST (February 2022)
|  | Comments | [16 empty] | Urban? Proximity of consumers? | Assessment of accessway and space for turning larger vehicles. | assume 4 x 4 m, review per previous report on poential UV equipment locations | Building expansion or new stand-alone building required | On site, on road (either side), none | Yes (likely) /no |  |  | 30 pipe diameters between metering chamber (point of injection) and sampling point (before 1st diversion)
PS# | Water Supply Zone | PS Name | PS Number | Include / Exclude | PS Type | Description | Suction Tank | Suction Tank Volume (m3) | No. Wells | No. Surface Pumps | Pump Size (m3/hr/pump) | Max historic Q (m3/hr) | PS Capacity Now (m3/hr) | PS Capacity Future (m3/hr) | CCC Notes | PS Capacity Now (ML/d) | PS Capacity Future (ML/d) | Part of City Care Assessment | Site Setting | Delivery Constraints | Site Expansion Footprint Constrains | New Building Required (Yes/No) | WW Connection On Site | Tree Removal Required | Distance from metering chamber to point of 1st diversion (m) | Pipe Diameter (mm) | Mixer Required | Eyewash Station Required | SCADA Upgrade Requierd | Constrained Site (Yes/No) | Site Comments | Jacobs notes
1 | North West | Thompsons | PS1078 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 377 | 350 | 350 |  | 8.4 | 8.4 |  | Urban | None | None | No | None | No | 9 | 300 | Yes | Yes |  |  | There is space on site for building expansion, good access Per Karn's comment on Thursday, this is "tight, landwise" | Close for mixer
| North West | Auburn | PS1068 | exclude - renewal | 2 | suction tank / surface pumped into mains | Yes |  | 1 | 2 | 140/140 | 327 | 275 | 0 | renewal planned for completion FY28 | 6.6 | 0
2 | North West | Avonhead | PS1069 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 374 | 374 | 374 |  | 8.976 | 8.976 |  | Urban | None | None | No | On-road | No | 7.4 | 375 | Yes | Yes |  |  | Sufficient space for building expansion. Good site access.
3 | North West | Belfast | PS1070 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 2 | 1 | 200 | 261 | 380 | 380 | changes made to station to achieve higher max | 9.12 | 9.12 |  | Urban | Minor | Medium | Yes | On-road | Yes | 27 | 300 | No | Yes |  |  | Tight accessway, no turning circle present, reversing only. Building expansion will block access to site. New building required.
4 | North West | Burnside | PS1071 | include | 1 | submersible pumped into mains | û |  | 6 | n/a |  | 779 | 845 | 845 |  | 20.28 | 20.28 |  | Public space | None | None | No | On-road (far) | Yes | 18 | 300 | No | Yes |  |  | Located within public park, plenty of space, consider extra precaution due to public access. | Complicated piping, check
5 | North West | Crosbie | PS1072 | include | 1 | submersible pumped into mains | û |  | 3 | n/a |  | 512 | 512 | 512 |  | 12.288 | 12.288 |  | Urban | Minor | None | Yes | On-road (far) | No | See note | 300 | No | Yes |  |  | Space available on site. Building expansion constrained, will require detached building. | Meter looks to be after a mains offtake. One bore goes straight to network and has a separate chlorine installation from the other two bores, slightly complicated for contact time. Therre is time before network but needs to be relocated prior to take off
6 | North West | Farrington | PS1073 | include | 1 | submersible pumped into mains | û |  | 5 | n/a |  | 918.5568 | 918.5568 | 918.5568 |  | 22.0454 | 22.0454 |  | Urban | None | None | No | On road | Yes | 7 | 300 | Yes | Yes |  |  | Tight accessway, sufficient space onsite adjacent to existing building for expansion.
7 | North West | Grampian | PS1074 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 160/160/130 | 430 | 430 | 450 |  | 10.32 | 10.8 | Yes | Urban | None | None | Yes | On road | No | 14 | 225 | No | Yes |  |  | Expansion space present but not near existing building so new building required. Space near the back of site.
8 | North West | Jeffreys | PS1076 | include | 2 | suction tank / surface pumped into mains | Yes | 450 | 4 | 2 | 140/140 250/250 future | 246 | 246 | 500 | suction tank being constructed / pumps upgraded | 5.904 | 12 |  | Urban | Minor | None | No | On road (far) | No | 15 | 300 | No | Yes |  |  | Room for expansion on building. Small turning circle and narrow long access way
9 | North West | Redwood | PS1077 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 535 | 0 | 424.8 | work underway to renew wells | 0 | 10.1952 |  | Urban | Medium | Medium | Yes | On road | Yes | 8 | 200 | No | Yes |  |  | Very small site. Will require removal of trees for additional building. Only room to drive in and back out of site off busy road. | Close for mixer
10 | North West | Wrights | PS1080 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 381 | 356 | 356 |  | 8.544 | 8.544 |  | Commercial | None | None | No | On road | Yes | 8 | 250 | Yes | Yes |  |  | Large site, lots of scape, large area for turning etc. | No meter present but close connection to roadside
11 | North West | Gardiners | PS1125 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 2 | 2 | 180/180 | 350 | 350 | 350 |  | 8.4 | 8.4 |  | Rural | None | None | No | On road (far) | No | >40 | assume 250 (PE355) | No | Yes |  |  | Large site, good delivery options, room for expansion
12 | Rawhiti | Aston | PS1004 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 169/169 | 285 | 285 | 285 |  | 6.84 | 6.84 | Yes | Urban | None | None | No | On-site | No | 6 | 200-300 | Yes | Yes |  |  | Good reversing back for delivery, potential room on site for building expansion
13 | Rawhiti | Effingham | PS1010 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225 | 445 | 321 | 321 |  | 7.704 | 7.704 |  | Urban | Minor | None | No | On road | No | 2 | 200 | Yes | Yes |  |  | Small access only to the front of the building, new building expansion round the back, good space.
14 | Rawhiti | Keyes | PS1119 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 180/200/200 | 593 | 580 | 580 |  | 13.92 | 13.92 | Yes | Urban | None | None | No | On road | No | Cannot see meter | 300 | No | Yes |  |  | Good access to site, should be space for building expansion, if not, plenty of room for new building. | Cannot see meter but long distance to mains on road, safely say no mixer required.
15 | Rawhiti | Lake Terrace | PS1023 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 2 | 260/225 | 829 | 485 | 485 |  | 11.64 | 11.64 |  | Urban | None | Medium | Yes | On road | No | 1 | 250 | Yes | Yes |  |  | Good delivery, constrained site with not much room for building expansion but should be sufficient for site expansion. | division immediately upstream of meter but does not see consumer for over 30 m on diversions
16 | Rawhiti | Carters | PS1008 | include | 2 | suction tank / surface pumped into mains | Yes |  | 4 | 2 | 225/225=450 | 580 | 551 | 551 |  | 13.224 | 13.224 | Yes | Urban | Medium | High | N/A | On road | Yes | 5.5 | 250 | Yes | Yes |  |  | Very small site. No room for building or site expansion. Poor delivery access. Very constrained site.
17 | Rawhiti | Estuary | PS1012 | include | 2 | suction tank / surface pumped into mains | Yes |  | 1 | 2 | 182/108=290 | 319 | 277 | 277 |  | 6.648 | 6.648 |  | Urban | Medium | High | N/A | On road | No | 15 | 200 | No | Yes |  |  | Very small site. No room for building or site expansion. Poor delivery access. Very constrained site.
| Rawhiti | Ben Rarere PS | PS1126 | exclude - future | 2 | suction tank / surface pumped into mains | Yes | 500 | 2 | 2 | 225/225 | n/a | 0 | 504 | PS being constructed | 0 | 12.096
18 | West | Sockburn | PS1109 | include | 2 | suction tank / surface pumped into mains | Yes | 4500 | 6 | 2 | 792/792 = 1584 | 1312 | 1320 | 1320 | another pump as standby - well capacity used for PS max | 31.68 | 31.68 |  | Commercial | None | None | No | On road (far) | No | 12 | 450 | Yes | Yes |  |  | Good site. Plenty of space. Easy delivery. Lots of room for building expansion. | Technically long pipelines after 1st diversion before consumers could mean no mixer but 2 no. analysers?
19 | West | Denton | PS1099 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 5 | 2 | 900/900 = 1,800 | 1099 | 1100 | 1100 | another pump as standby - well capacity used for PS max | 26.4 | 26.4 |  | Semi-urban | Minor | None | No | On road (far) | No | Cannot see meter | 375 | No | Yes |  |  | Good space on site for building expansion. Slightly difficult access with long thin access road. No turning circle etc. | Cannot see meter but long distance to mains on road, safely say no mixer required.
20 | West | Wilmers | PS1117 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 2 | 3 | 400/780/780 = 1,960 | 1254 | 470 | 470 | well capacity used for PS max - will be expanded in future | 11.28 | 11.28 |  | Urban | None | Minor | Yes | None | Yes | Cannot see meter | 500 | ? | Yes |  |  | Suitable space for site expansion but will be difficult for a building expansion potentially. Difficult access for chemical delivery. | 18 m post pumps but no sign of meter chmaber for dosing? Probably doesn’t need mixer check
21 | West | Dunbars | PS1102 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 4 | 2 | 900/900 = 1,800 | 1433 | 1149.984 | 1149.984 | another pump as standby - well capacity used for PS max | 27.5996 | 27.5996 |  | Urban | Minor | None | No | On road | No | 18 | 450 | No | Yes |  |  | Slightly tight delivery circle, plenty of space for building expansion.
22 | Central | Main Pumps WS | PS1024 | include | 2 | suction tank / surface pumped into mains | Yes | 1085 | 6 | 3 | 225/450/500=1,175 | 1138 | 1000 | 1000 |  | 24 | 24 |  | ?? |  | No | No | On road | No | Cannot see meter | 300 | No | Yes |  |  | Cannot find | Cannot see meter but long distance to mains on road, check
23 | Central | Addington | PS1001 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 260 | 252 | 252 |  | 6.048 | 6.048 |  | Urban | Minor | Medium | No | On road | Yes | 5 | 300 | Yes | Yes |  |  | Small site. Minimal delivery space for vehicles. Small area for building expansion which may be suitable. Difficult satellite imagery to tell how much space is available.
24 | Central | Aldwins | PS1002 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 230/230=460 | 287 | 280 | 280 | max PS capacity before becoming airlocked | 6.72 | 6.72 | Yes | Urban | None | None | No | On road | No | 7.7 | 300 | Yes | Yes |  |  | Good site. Plenty of space. Wide delivery access. Simple building expansion.
| Central | Averill | PS1005 | exclude - renewal | 4 | artesian/surface pumped into mains | û |  | 2 | 1 | 225 | 305 | 225 | 0 | renewal planned for completion FY26 | 5.4 | 0 | Yes
25 | Central | Blighs | PS1007 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 2 | 1 | 225 | 286 | 280 | 280 | 1 of wells being developed | 6.72 | 6.72 |  | Urban | None | None | No | On road | Yes | 20 | 200 | No | Yes |  |  | Compact site. Suitable space for building expansion. Delivery is reverse in and back out.
26 | Central | Grassmere | PS1014 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 528 | 528 | 528 |  | 12.672 | 12.672 |  | Urban | Minor | Medium | No | On road | No | 9 | 200 | No | Yes |  |  | Small space approx. 12-14 m2 for building expansion. Separate building would be difficult on site if this doesn’t work. Delivery is minor constraint with little space.
27 | Central | Hillmorton | PS1016 | include | 2 | suction tank / surface pumped into mains | Yes | 310 | 2 | 1 | 225 | 313 | 300 | 300 |  | 7.2 | 7.2 |  | Urban | Minor | High | Yes | On road | No | 22 | 300 | No | Yes |  |  | Very small site. Constrained for building expansion near current pump room. Small delivery bay present.
28 | Central | Hills | PS1017 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 622 | 580 | 580 |  | 13.92 | 13.92 |  | Urban | None | High | Minor | On road | No | 5 | 200-300 | Yes | Yes |  |  | Building expansion will be tight, there is space around site however. Could remove scrub to make space on building. Small delivery bay present
| Central | Kerrs | PS1022 | exclude - renewal | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225=450 | 410 | 345.625 | 345.625 | renewal planned for completion FY27 | 8.295 | 8.295
29 | Central | Mays | PS1026 | include | 2 | suction tank / surface pumped into mains | Yes | 350 | 3 | 2 | 225/225=450 | 551 | 225 | 550 | 3'rd well being developed | 5.4 | 13.2 |  | Urban | Minor | High | Yes | On site | No | 6 | 300 | Yes | Yes |  |  | Very constrained site. Small delivery access road. Building expansion very limited but some space elsewhere on site.
30 | Central | Montreal | PS1027 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 449 | 449 | 449 |  | 10.776 | 10.776 |  | Urban | None | Minor | No | On road | No | Cannot see meter | 200 | Yes | Yes |  |  | Space around the side of the building for expansion. Construction is narrow corridor of space could be difficult. | Cannot see meter but very close to roadsite and connections. Expeceted less than 5 metres so mixer
31 | Central | Spreydon | PS1030 | include | 2 | suction tank / surface pumped into mains | Yes |  | 5 | 2 | 225/225=450 | 455 | 225 | 450 | 2 wells being developed | 5.4 | 10.8 |  | Urban | None | None | No | On road | Yes | Cannot see meter | 200 | Yes | Yes |  |  | Delivery space on the smaller side. Plenty of space for building expansion etc. | Cannot see meter but very close to roadsite and connections. Expeceted less than 6 metres so mixer
32 | Central | Sydenham | PS1031 | include | 2 | suction tank / surface pumped into mains | Yes | 315 | 4 | 2 | 225/225=450 | 487 | 450 | 450 | suction tank being renewed | 10.8 | 10.8 |  | Commercial | None | None | No | On road (far) | No | 3 | 200 | Yes | Yes |  |  | Commercial site with plenty of space for both delivery and building expansion. | Technically long pipelines after 1st diversion before consumers could mean no mixer but 2 no. analysers?
33 | Central | Trafalgar | PS1035 | include | 2 | suction tank / surface pumped into mains | Yes | 250 | 3 | 2 | 225/225=450 | 510 | 450 | 450 |  | 10.8 | 10.8 |  | Urban | Medium | None | No | On road (far) | No | >50 | 250 | No | Yes |  |  | Site with plenty of space. Only constraint is very thin access road by past residential propoerties. | Very long accessway before connection
34 | Central | Worcester | PS1037 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225=450 | 511 | 511 | 511 |  | 12.264 | 12.264 |  | Urban | Minor | Medium | Yes | On road | Yes | Cannot see meter | 375 | No | Yes |  |  | Thin access site passing residential properties. Any building expansion will block access to site unless trees etc are removed at the back of the site. | Cannot see meter but minimum 30 m to main on road (not 1st diversion)
35 | Central | Tanner | PS1095 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 137 | 137 | 137 |  | 3.288 | 3.288 |  | Urban | None | None | No | On road | Yes | >50 (offsite) | 200 | No | Yes |  |  | Small building, large site for expansion. Huge space for delivery. | Site pipe to retic has no consumers till further down street so could be worth installating mixer incase new connections earlier in line.
36 | Riccarton | Picton | PS1088 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 3 | 2 | 220/220 +190 = 630 | 557.6776 | 557.6776 | 557.6776 |  | 13.3843 | 13.3843 |  | Urban | Minor | None | No | On road (far) | No | >50 | 300 | No | Yes |  |  | Tight access with small turning circle near children playground. Space for building expansion with plenty of room. | Note that we have sand filter post metering chamber
37 | Riccarton | Tara | PS1089 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 249 | 120 | 120 |  | 2.88 | 2.88 |  | Urban | None | ?? | No | On road | Yes | 5 | 200 | Yes | Yes |  |  | Not sure where the current delivery is located. Minimal access on satelliate. Open site with extensive room for expansion as required. | Not sure where dosing location is. Currently measured from M chmaber but Cl tank is closer to bore. If dosing is closer to bore, then no mixer required.
38 | Ferrymead | St Johns | PS1063 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 3 | 2 | 225/450=675 | 634 | 666.6667 | 666.6667 | max PS capacity = well consent | 16 | 16 |  | Urban | None | None | No | On road | Yes | <5 | 300 | Yes | Yes |  |  | There is space on site for building expansion and delivery is adjacent to the road curb.
39 | Ferrymead | Woolston | PS1065 | include | 2 | suction tank / surface pumped into mains | Yes | 400 | 3 | 3 | 250/250/250=750 | 639 | 545 | 545 |  | 13.08 | 13.08 | Yes | Urban | Medium | Medium | No | On road | Yes | Cannot see meter | 250 | ? | Yes |  |  | There is a small section of small to the front of the building which is the only section available. Approx 10 m2 of space. | Cannot see meter but very close to 1st diversion connections. Expeceted less than 5 metres so mixer
| Parklands | Burwood | PS1081 | exclude - remove | 4 | artesian/surface pumped into mains | û |  | 2 | 3 | 45/95/275 = 415 | 352 | 0 | 0 | planning underway to decommision | 0 | 0 | Yes
| Parklands | Mairehau | PS1083 | exclude - remove | 4 | artesian/surface pumped into mains | û |  | 1 | 1 | 270 | 241 | 0 | 0 | planning underway to decommision | 0 | 0
40 | Parklands | Marshlands | PS1084 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 220/220 = 440 | 412 | 440 | 440 |  | 10.56 | 10.56 |  | Urban | Minor | None | No | On road (far) | No | 19 | 300 | No | Yes |  |  | There is space on site for building expansion and delivery to the front of the building down reasonably tight access road. | Note that we have sand filter post metering chamber
41 | Parklands | Parklands | PS1085 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 3 | 164/355/200 = 719 | 499 | 500 | 500 |  | 12 | 12 |  | Urban | Minor | None | No | On road (far) | No | >50 | 300 | No | Yes |  |  | There is space on site for building expansion and delivery down reasonably tight access road.
42 | Parklands | Prestons | PS1123 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 4 | 3 | 200/200/200 = 600 | 768 | 768 | 768 |  | 18.432 | 18.432 |  | Urban | None | None | No | On road | No | Cannot see meter | 300 | No | Yes |  |  | Good size site. Plenty of space for building expansion and delivery to site. No contraints. | No meter on file but good distance to main on road. No mixer
43 | Kainga/Brooklands | Brooklands | PS1066 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 142 | 180 | 180 |  | 4.32 | 4.32 |  | Rural | None | None | No | On road | Yes | 25 | 200 | No | Yes |  |  | No issue with space or delivery to site. Good wide access and plnety of space to expand.
44 | Kainga/Brooklands | Kainga | PS1067 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 112 | 108 | 108 |  | 2.592 | 2.592 |  | Urban | None | None | No | On site | No | >30 | 200 | No | Yes |  |  | No issue with space or delivery to site. Good wide access and plnety of space to expand.
45 |  | Akaroa L’Aube Hill WTP | TP? | include | [8 empty] | 87.5 | 87.5 | comprises two membrane skids with minimum capacity of 400 m3/day and maximum 2,100 m3/day. | 2.1 | 2.1 | [10 empty] | Yes |  |  | Cannot locate | added per email from Michele McDonald
|  | Duvauchelle WTP | TP3505 | exclude | [13 empty] | Yes | [12 empty] | not part of this assignment, but was part of the previous City Care assessment
[5 empty] | 1 | submersible pumped into mains
[5 empty] | 2 | suction tank / surface pumped into mains
[5 empty] | 3 | submersible + artesian/surface pumped into mains
[5 empty] | 4 | artesian/surface pumped into mains
Note on T3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Located with urban area or semi-rural. close to consumers etc.
Note on U3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Assessment of accessway and space for turning larger vehicles.
Note on V3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is the current site boundary suitable for additional 4x4 area anywhere
Note on W3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Is there space for building expansion or will a new detached building be required
Note on AF27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: have a look at the water supply overview schematic. Looks like it's between Thorrington and Palatine

## Filtec Costing Raw (hidden)
Variables |  |  |  |  | Assumptions
Population Served | 10k-20k | 20k-30k | 50k-100k | 100k-150k
Capacity (m3/day) | 6000 | 15000 | 30000 | 45000 | 300 L/d/p
Equipment including Installation
Analyser | 17500 | 17500 | 17500 | 17500
Safety shower | 7000 | 7000 | 7000 | 7000
HAZOP | 7500 | 7500 | 7500 | 7500
Storage tank capacity (l) | 600 | 1500 | 3200 | 6500
Storage tank | 7500 | 10000 | 12500 | 15000 | 30 days
Day tank capacity | 20 | 50 | 100 | 200
Day tank | 1500 | 3000 | 5000 | 8000
Transfer pump | 5000 | 7500 | 10000 | 12500
Dosing pump/pipework | 15000 | 29000 | 43000 | 58000
Flowmeter | 15000 | 17500 | 20000 | 22500
Installation and commissioning | 43000 | 50000 | 58000 | 65000
Electrical and automation | 36000 | 40000 | 43000 | 46000
Total 20% | 156000 | 191000 | 227000 | 266000
Exclusions | [5 empty] | m3/day | m3/hr | cost
Freight to site | [5 empty] | 6000 | 250 | 156000
Civil works | [5 empty] | 15000 | 625 | 191000
Building upgrades | [5 empty] | 30000 | 1250 | 227000
Bunding | [5 empty] | 45000 | 1875 | 266000
SCADA upgrade and integration
On-line monitoring operational costs | [6 empty] | 300 | 163885.4
HFA supply | [6 empty] | 1320 | 231080.96
HFA unloading system
Operator costs
Maintenance
Injection point pipework
Duty dosing pump only
Ventilation
Waste disposal
Plant security
Heating (HFA freezes at 0°C)
HSNO compliance
Power connection

## DPCache_Original PS List (hidden)
PS# | Water Supply Zone | PS Name | PS Number | Include / Exclude | PS Type | Description | Suction Tank | Suction Tank Volume (m3) | No. Wells | No. Surface Pumps | Pump Size (m3/hr/pump) | Max historic Q (m3/hr) | PS Capacity Now (m3/hr) | PS Capacity Future (m3/hr) | Notes | PS Capacity Now (ML/d) | PS Capacity Future (ML/d)
1 | North West | Thompsons | PS1078 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 377 | 350 | 350 |  | 8.4 | 8.4
| North West | Auburn | PS1068 | exclude - renewal | 2 | suction tank / surface pumped into mains | Yes |  | 1 | 2 | 140/140 | 327 | 275 | 0 | renewal planned for completion FY28 | 6.6 | 0
2 | North West | Avonhead | PS1069 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 374 | 374 | 374 |  | 8.976 | 8.976
3 | North West | Belfast | PS1070 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 2 | 1 | 200 | 261 | 380 | 380 | changes made to station to achieve higher max | 9.12 | 9.12
4 | North West | Burnside | PS1071 | include | 1 | submersible pumped into mains | û |  | 6 | n/a |  | 779 | 845 | 845 |  | 20.28 | 20.28
5 | North West | Crosbie | PS1072 | include | 1 | submersible pumped into mains | û |  | 3 | n/a |  | 512 | 512 | 512 |  | 12.288 | 12.288
6 | North West | Farrington | PS1073 | include | 1 | submersible pumped into mains | û |  | 5 | n/a |  | 918.5568 | 918.5568 | 918.5568 |  | 22.0454 | 22.0454
7 | North West | Grampian | PS1074 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 160/160/130 | 430 | 430 | 450 |  | 10.32 | 10.8
8 | North West | Jeffreys | PS1076 | include | 2 | suction tank / surface pumped into mains | Yes | 450 | 4 | 2 | 140/140 250/250 future | 246 | 246 | 500 | suction tank being constructed / pumps upgraded | 5.904 | 12
9 | North West | Redwood | PS1077 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 535 | 0 | 424.8 | work underway to renew wells | 0 | 10.1952
10 | North West | Wrights | PS1080 | include | 1 | submersible pumped into mains | û |  | 2 | n/a |  | 381 | 356 | 356 |  | 8.544 | 8.544
11 | North West | Gardiners | PS1125 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 2 | 2 | 180/180 | 350 | 350 | 350 |  | 8.4 | 8.4
12 | Rawhiti | Aston | PS1004 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 169/169 | 285 | 285 | 285 |  | 6.84 | 6.84
13 | Rawhiti | Effingham | PS1010 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225 | 445 | 321 | 321 |  | 7.704 | 7.704
14 | Rawhiti | Keyes | PS1119 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 3 | 180/200/200 | 593 | 580 | 580 |  | 13.92 | 13.92
15 | Rawhiti | Lake Terrace | PS1023 | include | 2 | suction tank / surface pumped into mains | Yes |  | 3 | 2 | 260/225 | 829 | 485 | 485 |  | 11.64 | 11.64
16 | Rawhiti | Carters | PS1008 | include | 2 | suction tank / surface pumped into mains | Yes |  | 4 | 2 | 225/225=450 | 580 | 551 | 551 |  | 13.224 | 13.224
17 | Rawhiti | Estuary | PS1012 | include | 2 | suction tank / surface pumped into mains | Yes |  | 1 | 2 | 182/108=290 | 319 | 277 | 277 |  | 6.648 | 6.648
| Rawhiti | Ben Rarere PS | PS1126 | exclude - future | 2 | suction tank / surface pumped into mains | Yes | 500 | 2 | 2 | 225/225 | n/a | 0 | 504 | PS being constructed | 0 | 12.096
18 | West | Sockburn | PS1109 | include | 2 | suction tank / surface pumped into mains | Yes | 4500 | 6 | 2 | 792/792 = 1584 | 1312 | 1320 | 1320 | another pump as standby - well capacity used for PS max | 31.68 | 31.68
19 | West | Denton | PS1099 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 5 | 2 | 900/900 = 1,800 | 1099 | 1100 | 1100 | another pump as standby - well capacity used for PS max | 26.4 | 26.4
20 | West | Wilmers | PS1117 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 2 | 3 | 400/780/780 = 1,960 | 1254 | 470 | 470 | well capacity used for PS max - will be expanded in future | 11.28 | 11.28
21 | West | Dunbars | PS1102 | include | 2 | suction tank / surface pumped into mains | Yes | 3500 | 4 | 2 | 900/900 = 1,800 | 1433 | 1149.984 | 1149.984 | another pump as standby - well capacity used for PS max | 27.5996 | 27.5996
22 | Central | Main Pumps WS | PS1024 | include | 2 | suction tank / surface pumped into mains | Yes | 1085 | 6 | 3 | 225/450/500=1,175 | 1138 | 1000 | 1000 |  | 24 | 24
23 | Central | Addington | PS1001 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 260 | 252 | 252 |  | 6.048 | 6.048
24 | Central | Aldwins | PS1002 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 230/230=460 | 287 | 280 | 280 | max PS capacity before becoming airlocked | 6.72 | 6.72
| Central | Averill | PS1005 | exclude - renewal | 4 | artesian/surface pumped into mains | û |  | 2 | 1 | 225 | 305 | 225 | 0 | renewal planned for completion FY26 | 5.4 | 0
25 | Central | Blighs | PS1007 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 2 | 1 | 225 | 286 | 280 | 280 | 1 of wells being developed | 6.72 | 6.72
26 | Central | Grassmere | PS1014 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 528 | 528 | 528 |  | 12.672 | 12.672
27 | Central | Hillmorton | PS1016 | include | 2 | suction tank / surface pumped into mains | Yes | 310 | 2 | 1 | 225 | 313 | 300 | 300 |  | 7.2 | 7.2
28 | Central | Hills | PS1017 | include | 2 | suction tank / surface pumped into mains | Yes | 300 | 3 | 2 | 225/225=450 | 622 | 580 | 580 |  | 13.92 | 13.92
| Central | Kerrs | PS1022 | exclude - renewal | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225=450 | 410 | 345.625 | 345.625 | renewal planned for completion FY27 | 8.295 | 8.295
29 | Central | Mays | PS1026 | include | 2 | suction tank / surface pumped into mains | Yes | 350 | 3 | 2 | 225/225=450 | 551 | 225 | 550 | 3'rd well being developed | 5.4 | 13.2
30 | Central | Montreal | PS1027 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 449 | 449 | 449 |  | 10.776 | 10.776
31 | Central | Spreydon | PS1030 | include | 2 | suction tank / surface pumped into mains | Yes |  | 5 | 2 | 225/225=450 | 455 | 225 | 450 | 2 wells being developed | 5.4 | 10.8
32 | Central | Sydenham | PS1031 | include | 2 | suction tank / surface pumped into mains | Yes | 315 | 4 | 2 | 225/225=450 | 487 | 450 | 450 | suction tank being renewed | 10.8 | 10.8
33 | Central | Trafalgar | PS1035 | include | 2 | suction tank / surface pumped into mains | Yes | 250 | 3 | 2 | 225/225=450 | 510 | 450 | 450 |  | 10.8 | 10.8
34 | Central | Worcester | PS1037 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 2 | 225/225=450 | 511 | 511 | 511 |  | 12.264 | 12.264
35 | Central | Tanner | PS1095 | include | 1 | submersible pumped into mains | û |  | 2 | n/a | n/a | 137 | 137 | 137 |  | 3.288 | 3.288
36 | Riccarton | Picton | PS1088 | include | 3 | submersible + artesian/surface pumped into mains | û |  | 3 | 2 | 220/220 +190 = 630 | 557.6776 | 557.6776 | 557.6776 |  | 13.3843 | 13.3843
37 | Riccarton | Tara | PS1089 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 249 | 120 | 120 |  | 2.88 | 2.88
38 | Ferrymead | St Johns | PS1063 | include | 2 | suction tank / surface pumped into mains | Yes | 180 | 3 | 2 | 225/450=675 | 634 | 666.6667 | 666.6667 | max PS capacity = well consent | 16 | 16
39 | Ferrymead | Woolston | PS1065 | include | 2 | suction tank / surface pumped into mains | Yes | 400 | 3 | 3 | 250/250/250=750 | 639 | 545 | 545 |  | 13.08 | 13.08
| Parklands | Burwood | PS1081 | exclude - remove | 4 | artesian/surface pumped into mains | û |  | 2 | 3 | 45/95/275 = 415 | 352 | 0 | 0 | planning underway to decommision | 0 | 0
| Parklands | Mairehau | PS1083 | exclude - remove | 4 | artesian/surface pumped into mains | û |  | 1 | 1 | 270 | 241 | 0 | 0 | planning underway to decommision | 0 | 0
40 | Parklands | Marshlands | PS1084 | include | 4 | artesian/surface pumped into mains | û |  | 2 | 2 | 220/220 = 440 | 412 | 440 | 440 |  | 10.56 | 10.56
41 | Parklands | Parklands | PS1085 | include | 4 | artesian/surface pumped into mains | û |  | 3 | 3 | 164/355/200 = 719 | 499 | 500 | 500 |  | 12 | 12
42 | Parklands | Prestons | PS1123 | include | 2 | suction tank / surface pumped into mains | Yes | 500 | 4 | 3 | 200/200/200 = 600 | 768 | 768 | 768 |  | 18.432 | 18.432
43 | Kainga/Brooklands | Brooklands | PS1066 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 142 | 180 | 180 |  | 4.32 | 4.32
44 | Kainga/Brooklands | Kainga | PS1067 | include | 1 | submersible pumped into mains | û |  | 1 | n/a | n/a | 112 | 108 | 108 |  | 2.592 | 2.592
45 |  | Akaroa L’Aube Hill WTP |  | include | [8 empty] | 87.5 | 87.5 | comprises two membrane skids with minimum capacity of 400 m3/day and maximum 2,100 m3/day. | 2.1 | 2.1